## Supply_Details
Private Water Supply: Risk Assessment tool
|  |  |  | Supply Name & Address: |  | V 3.07
Local Authority: | Local Authority: | Supply Reference: | Supply Reference: | Supply Name & Address:
Estimated daily volume of water supplied (m3 per day): |  | Normal number of consumers served (maximum): |  | Date of Risk Assessment:
| Local Authority: Supply Reference: | Supply Name & Address:
Regulation Supply Type: |  |  |  |  | Assessor:
Addresses of connected sites
Name of person / organisation | Relevance | Telephone number | Address | Email | Purpose | Comments
Description of Supply
Details of source |  | Location |  | Grid reference
Details of any water treatment processes present:
Other: please enter details
Diagram of supply
Insert hyperlink or file location Resize box if required
Manuals, SOP's, Instructions for use
Insert hyperlink or file location Resize box if required
Details of departures authorised
Please enter details: Resize box if required
Summary of previous sample results
Please enter details: Resize box if required
Summary of details of previous investigations and actions taken
Please enter details: Resize box if required
Details of previous/existing enforcement notices served
Please enter details: Resize box if required
Result of previous risk assessment (if applicable)
Please enter details: Resize box if required
Details of action taken (or to be taken) by relevant persons in respect of investigation
Please enter details: Resize box if required
Any additional relevant details or other information relating to the supply:
Please enter details: Resize box if required

## Risk_Assessment
Private Water Supply: Risk Assessment tool
[6 empty] | Local Authority: |  |  |  | Supply Reference:
[6 empty] | Supply Name & Address: |  |  |  | 0
[6 empty] | Hazard Guidance - |  |  |  | Select Risk number: |  | A5
Operators should be competent in the operation of the supply system they are managing, and have an understanding of the need to apply sound hygienic practice. A lack of competency and/or hygiene awareness presents a risk of contamination of the supply. The risk assessor must determine what and when training has been undertaken, and whether it is appropriate. For a complex treatment system such as chlorination or chlorine dioxide disinfection a formal training course maybe required, whereas for a UV system informal training form the supplier with written procedures could be appropriate. This can be achieved through dialogue and evidence through certification or other written records. A judgement as to whether deficiencies present a risk must be made and relevant advice provided.
Risk | High risks | V High risks | Medium Risks | Low risks | TBC | Risk No. | Hazard Description | Yes/No |  | Likelihood | Severity | Risk | Comments
A - General Overview
TBC1 | H0 | VH0 | M0 | L0 | TBC1 | A0 | Have there been any changes since risk assessment last carried out? | TBC |  | 5 |  | TBC
TBC2 | H0 | VH0 | M0 | L0 | TBC2 | A1 | Is there a site plan and/or schematic showing location of source, chambers, tanks, distribution network including valves, pipes, consumer premises etc.? | TBC |  | 5 | 5 | TBC |  | 1 | Yes | TBC | 5x5 Risk scoring
TBC3 | H0 | VH0 | M0 | L0 | TBC3 | A2 | Are there any procedures and/or written records for the supply (i.e. for checks, monitoring or maintenance, etc.)? | TBC |  | 5 | 5 | TBC |  | 2 | No | L | Low |  | < | 6
TBC4 | H0 | VH0 | M0 | L0 | TBC4 | A3 | Are there any manufacturers' instructions for the equipment on the supply? | TBC |  | 5 | 5 | TBC |  | 3 | TBC | M | Medium | 6 | to | 11
TBC5 | H0 | VH0 | M0 | L0 | TBC5 | A4 | Is there an emergency plan for the provision of an alternative water supply? | TBC |  | 5 | 5 | TBC |  | 4 | N/A | H | High | 11 |  | 15
TBC6 | H0 | VH0 | M0 | L0 | TBC6 | A5 | Has the owner or operators had appropriate training for the supply? | TBC |  | 5 | 5 | TBC |  | 5 |  | VH | V. High |  | > | 15
TBC7 | H0 | VH0 | M0 | L0 | TBC7 | A6 | Does the sampling history identify the presence of any hazards? | TBC |  | 5 | 3 | TBC
Section B - SOURCE: All catchments
TBC8 | H0 | VH0 | M0 | L0 | TBC8 | B1 | Are there latrines, septic tanks, animal enclosures or cess pits present within 50m of the source? | TBC |  |  | 4 | TBC
TBC9 | H0 | VH0 | M0 | L0 | TBC9 | B2 | Are there any waste pipes (sewage) adjacent to the source? | TBC |  |  | 4 | TBC
TBC10 | H0 | VH0 | M0 | L0 | TBC10 | B3 | Is there a risk of microbial contamination (from slurry spreading, and/or storage of slurry or dung)? | TBC |  |  | 5 | TBC
TBC11 | H0 | VH0 | M0 | L0 | TBC11 | B4 | Is there a risk of pesticides or chemical contamination (e.g. sheep dipping chemicals) | TBC |  |  | 4 | TBC
TBC12 | H0 | VH0 | M0 | L0 | TBC12 | B5 | Are chemical fertilisers used? | TBC |  |  | 4 | TBC
TBC13 | H0 | VH0 | M0 | L0 | TBC13 | B6 | Is there history of mining in the catchment (i.e. chemical or metal contamination)? | TBC |  |  | 4 | TBC
TBC14 | H0 | VH0 | M0 | L0 | TBC14 | B7 | Does the local geology suggest the present of - boron, arsenic, lead, fluoride, uranium, nickel, radon or other potentially harmful natural substance in raw water? | TBC |  |  | 4 | TBC
TBC15 | H0 | VH0 | M0 | L0 | TBC15 | B8 | Is the source likely to be affected by any contaminated land including landfill sites in the catchment? | TBC |  |  | 4 | TBC
TBC16 | H0 | VH0 | M0 | L0 | TBC16 | B9 | Is there a likelihood of insufficiency of supply i.e. over-abstraction of source or during drought conditions | TBC |  |  | 4 | TBC
TBC17 | H0 | VH0 | M0 | L0 | TBC17 | B10 | Is the source adequately protected against vandalism (deliberate contamination of source and unauthorised access)? | TBC |  |  | 5 | TBC
TBC18 | H0 | VH0 | M0 | L0 | TBC18 | B11 | Is there a risk of oil spill entering the supply (e.g. generators, household heating oil, farm fuel, generators, road traffic accident or the presence of a redundant tanker etc.)? | TBC |  |  | 5 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC18 | B12 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC18 | B13 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC18 | B14 |  | N/A | N/A
Section B - Radioactivity
TBC19 | H0 | VH0 | M0 | L0 | TBC19 | B15 | Are there any man made sources of tritium in the catchment which could affect the water supply? | TBC |  |  | 5 | TBC
TBC20 | H0 | VH0 | M0 | L0 | TBC20 | B16 | Has the Environment Agency any record of historic pollution event(s) in the catchment which contained radioactive substances? | TBC |  |  | 5 | TBC
TBC21 | H0 | VH0 | M0 | L0 | TBC21 | B17 | Does the local water company have a notice allowing them to cease monitoring for tritium or ID for abstraction points from the same aquifer? | TBC |  |  | 5 | TBC
TBC22 | H0 | VH0 | M0 | L0 | TBC22 | B18 | Is there any monitoring data (EA/Wco/LA) for radioactive substances in this supply or another supply in the same water body indicating levels above the standard/value? | TBC |  |  | 5 | TBC
TBC23 | H0 | VH0 | M0 | L0 | TBC23 | B19 | Does the ‘Radioactivity in Food and the environment’ report indicate the likely presence of radioactive substances? | TBC |  |  | 4 | TBC
TBC24 | H0 | VH0 | M0 | L0 | TBC24 | B20 | If gross alpha or gross beta exceed the limit, does the Indicative Dose (ID)calculation confirm the value is <0.1mSv? | TBC |  |  | 5 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC24 | B21 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC24 | B22 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC24 | B23 |  | N/A | N/A
Section C - SOURCE: Catchment of Surface Water Supply (including springs)
TBC25 | H0 | VH0 | M0 | L0 | TBC25 | C1 | Is there a noticeable change in the appearance of the water from time to time (colour, cloudiness/turbidity)? | TBC |  |  | 4 | TBC
TBC26 | H0 | VH0 | M0 | L0 | TBC26 | C2 | Is the source exposed to risks of faecal contamination from wildlife (this will always be yes for all surface water sources, i.e. rivers, lakes and streams)? | TBC |  |  | 3 | TBC
TBC27 | H0 | VH0 | M0 | L0 | TBC27 | C3 | Is there waste-water discharging biological matter into the source? | TBC |  |  | 5 | TBC
TBC28 | H0 | VH0 | M0 | L0 | TBC28 | C4 | Is there waste-water discharging chemical substances into the source? | TBC |  |  | 4 | TBC
TBC29 | H0 | VH0 | M0 | L0 | TBC29 | C5 | Are there unbunded stores of farm waste or silage in the catchment? | TBC |  |  | 5 | TBC
TBC30 | H0 | VH0 | M0 | L0 | TBC30 | C6 | Is local forestry activity causing or likely to cause suspended particles in the source water? | TBC |  |  | 3 | TBC
TBC31 | H0 | VH0 | M0 | L0 | TBC31 | C7 | Is freshwater aquaculture practised upstream, causing contamination (feed, pesticides etc.)? | TBC |  |  | 4 | TBC
TBC32 | H0 | VH0 | M0 | L0 | TBC32 | C8 | Is there run off from construction/development activities upstream of intake causing contamination (oil spills, silt, cement, bentonites, soakaways, open tanks, surface water inceptors)? | TBC |  |  | 4 | TBC
TBC33 | H0 | VH0 | M0 | L0 | TBC33 | C9 | Is local quarrying activity causing or likely to cause suspended particles or any chemicals in the source water? | TBC |  |  | 4 | TBC
TBC34 | H0 | VH0 | M0 | L0 | TBC34 | C10 | Is the source water used for recreational purposes? | TBC |  |  | 4 | TBC
TBC35 | H0 | VH0 | M0 | L0 | TBC35 | C11 | Is the source water subject to seasonal algal blooms including toxin producing algae (cyanobacteria)? | TBC |  |  | 3 | TBC
TBC36 | H0 | VH0 | M0 | L0 | TBC36 | C12 | Is the spring chamber designed and constructed to exclude surface water or spillages of contaminated material causing microbial or other contamination (through the cover or the lining) and is it in a satisfactory state of repair? | TBC |  |  | 5 | TBC
TBC37 | H0 | VH0 | M0 | L0 | TBC37 | C13 | Does the spring chamber extend at least 150mm above the level of the floor with an apron sloping away from a secure cover? | TBC |  |  | 5 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC37 | C14 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC37 | C15 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC37 | C16 |  | N/A | N/A
Section D - SOURCE: Catchment of Ground Water Supply
TBC38 | H0 | VH0 | M0 | L0 | TBC38 | D1 | Where there are abandoned wells or observation boreholes are they adequately capped, fenced and protected? | TBC |  |  | 4 | TBC
TBC39 | H0 | VH0 | M0 | L0 | TBC39 | D2 | Are livestock excluded from the vicinity of the headworks (e.g. by fencing) to minimise the risk of microbial contamination? | TBC |  |  | 5 | TBC
TBC40 | H0 | VH0 | M0 | L0 | TBC40 | D3 | Is there evidence of standing water/ponding within 50m of the headworks? | TBC |  |  | 4 | TBC
TBC41 | H0 | VH0 | M0 | L0 | TBC41 | D4 | Is the borehole or well appropriately lined with casing and grouted to prevent ingress of shallow subsurface and/or surface water? | TBC |  |  | 4 | TBC
TBC42 | H0 | VH0 | M0 | L0 | TBC42 | D5 | If a chamber is present does it have barrier(s) to prevent ingress of surface water through the walls/floor (grouting/diversion ditch/walls etc.)? | TBC |  |  | 5 | TBC
TBC43 | H0 | VH0 | M0 | L0 | TBC43 | D6 | If a chamber is present does it have a cover that is non-degradable material that would prevent ingress of rainwater, vermin and is lockable (if not inside a locked building)? | TBC |  |  | 5 | TBC
TBC44 | H0 | VH0 | M0 | L0 | TBC44 | D7 | Are the headworks completely sealed so that no surface water, spillages or vermin/insects can enter? | TBC |  |  | 4 | TBC
TBC45 | H0 | VH0 | M0 | L0 | TBC45 | D8 | Are there land drains which channel water into the source? | TBC |  |  | 5 | TBC
TBC46 | H0 | VH0 | M0 | L0 | TBC46 | D9 | Are there historic results from the supply confirming the radon levels are below 100Bq/l? | TBC |  |  | 5 | TBC
TBC47 | H0 | VH0 | M0 | L0 | TBC47 | D10 | Does the local water company have a waiver for radon for abstraction points in the same aquifer? | TBC |  |  | 5 | TBC
TBC48 | H0 | VH0 | M0 | L0 | TBC48 | D11 | Do radon-in-air measurements confirm the levels are below 200Bq/m3 (where there is no existing radon treatment)? | TBC |  |  | 4 | TBC
TBC49 | H0 | VH0 | M0 | L0 | TBC49 | D12 | Does the PHE report or AEA Ricardo report identify the site as moderate or high hazards rating? | TBC |  |  | 4 | TBC
TBC50 | H0 | VH0 | M0 | L0 | TBC50 | D13 | Do sample results indicate radon levels are greater than 1000Bq/l? | TBC |  |  | 5 | TBC
TBC51 | H0 | VH0 | M0 | L0 | TBC51 | D14 | Is the source exposed to risks of faecal contamination from wildlife | TBC |  |  | 5 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC51 | D15 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC51 | D16 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC51 | D17 |  | N/A | N/A
Section E - SOURCE: Mains water supplied by means of pipes (Regulation 8 supplies)
TBC52 | H0 | VH0 | M0 | L0 | TBC52 | E1 | Is there evidence the supply main is coal tar lined? | TBC |  |  | 4 | TBC
TBC53 | H0 | VH0 | M0 | L0 | TBC53 | E2 | Are there sediments in the main? | TBC |  |  | 3 | TBC
TBC54 | H0 | VH0 | M0 | L0 | TBC54 | E3 | Is the section of main upstream of the point of supply subject to good turnover of water (e.g. are there connections to properties nearby which would ensure the water is refreshed in the main constantly)? | TBC |  |  | 3 | TBC
TBC55 | H0 | VH0 | M0 | L0 | TBC55 | E4 | If the area feeding the supply has had water quality related complaints in the last 12 months, have the causes been mitigated? | TBC |  |  | 3 | TBC
TBC56 | H0 | VH0 | M0 | L0 | TBC56 | E5 | Have any chemical parameters exceeded the standard in the previous 12 months in the mains supply? | TBC |  |  | 5 | TBC
TBC57 | H0 | VH0 | M0 | L0 | TBC57 | E6 | Are there backflow protection deficiencies at any upstream industrial or commercial premises? | TBC |  |  | 4 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC57 | E7 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC57 | E8 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC57 | E9 |  | N/A | N/A
[6 empty] | Section F - This section has been left blank intentionally. |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC57 | F1 | Is the supplier/contractor competent to undertake the requirements of BS 8551 - Provision and management of temporary supplies and distribution networks.? | N/A | N/A |  | 5
FALSE | H0 | VH0 | M0 | L0 | TBC57 | F2 | Is the tanker suitable in accordance with BS 8551? | N/A | N/A |  | 5
FALSE | H0 | VH0 | M0 | L0 | TBC57 | F3 | Has the tanker been used exclusively for water (i.e. not previously used for milk)? | N/A | N/A |  | 5
FALSE | H0 | VH0 | M0 | L0 | TBC57 | F4 | Has the tanker been cleaned and disinfected as specified in BS 8551? | N/A | N/A |  | 5
FALSE | H0 | VH0 | M0 | L0 | TBC57 | F5 | Are records available to demonstrate activities have been undertaken in accordance with BS 8551? | N/A | N/A |  | 5
FALSE | H0 | VH0 | M0 | L0 | TBC57 | F6 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC57 | F7 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC57 | F8 |  | N/A | N/A
[6 empty] | Section G - This section has been left blank intentionally. |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC57 | G1 | Does the supplier/contractor operate in accordance with BS 8551? | N/A | N/A |  | 5
FALSE | H0 | VH0 | M0 | L0 | TBC57 | G2 | Is the temporary water storage facility suitable in accordance with BS 8551? | N/A | N/A |  | 5
FALSE | H0 | VH0 | M0 | L0 | TBC57 | G3 | Has the temporary water storage facility previously been used exclusively for water (i.e. not previously used for milk)? | N/A | N/A |  | 5
FALSE | H0 | VH0 | M0 | L0 | TBC57 | G4 | Has the temporary water storage facility been cleaned and disinfected as specified in BS 8551? | N/A | N/A |  | 5
FALSE | H0 | VH0 | M0 | L0 | TBC57 | G5 | Does the source water originate from a wholesome supply i.e. a wholesome mains water/borehole/well/spring? | N/A | N/A |  | 5
FALSE | H0 | VH0 | M0 | L0 | TBC57 | G6 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC57 | G7 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC57 | G8 |  | N/A | N/A
[6 empty] | Section H - This section has been left blank intentionally. |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC57 | H1 | Are the hoses used for filling clean, and suitable according to BS8551? | N/A | N/A |  | 5
FALSE | H0 | VH0 | M0 | L0 | TBC57 | H2 | Are the hoses used for filling stored off the ground on a reel and capped off? | N/A | N/A |  | 5
FALSE | H0 | VH0 | M0 | L0 | TBC57 | H3 | Are the outlets of the tank or tanker protected (bagged) and sealed? | N/A | N/A |  | 5
FALSE | H0 | VH0 | M0 | L0 | TBC57 | H4 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC57 | H5 |  | N/A | N/A
Section I - SOURCE: Rainwater harvesting
TBC58 | H0 | VH0 | M0 | L0 | TBC58 | I1 | Is there any protection against faecal or chemical contamination e.g. from wildlife or industrial emissions? | TBC |  |  | 5 | TBC
TBC59 | H0 | VH0 | M0 | L0 | TBC59 | I2 | Are there any screens to prevent material entering the collection chamber (e.g. leaves, insects, twigs)? | TBC |  |  | 4 | TBC
TBC60 | H0 | VH0 | M0 | L0 | TBC60 | I3 | Are there any trees overhanging the roof? | TBC |  |  | 4 | TBC
TBC61 | H0 | VH0 | M0 | L0 | TBC61 | I4 | Is there evidence of lead, tin, copper, asphalt, new galvanised sheeting or wood preservatives on the roof? | TBC |  |  | 4 | TBC
TBC62 | H0 | VH0 | M0 | L0 | TBC62 | I5 | Is there a bypass mechanism to exclude the first flush of rainwater from the roof? | TBC |  |  | 5 | TBC
TBC63 | H0 | VH0 | M0 | L0 | TBC63 | I6 | Is there adequate backflow protection for any rainwater harvesting systems in place at any of the properties? | TBC |  |  | 5 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC63 | I7 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC63 | I8 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC63 | I9 |  | N/A | N/A
[6 empty] | Section J - SOURCE: Surface Water Intake (excluding springs) |  |  | H
TBC64 | H0 | VH0 | M0 | L0 | TBC64 | J1 | Does the water quality vary at the intake point due to streaming/stratification/algal blooms/increased turbidity? | TBC |  |  | 3 | TBC
TBC65 | H0 | VH0 | M0 | L0 | TBC65 | J2 | Are there screens in place at the intake? | TBC |  |  | 3 | TBC
TBC66 | H0 | VH0 | M0 | L0 | TBC66 | J3 | Where screens are present, is there a mechanism to remove debris? | TBC |  |  | 3 | TBC
TBC67 | H0 | VH0 | M0 | L0 | TBC67 | J4 | Does sediment build up inside the chamber and pipework after the intake point? | TBC |  |  | 3 | TBC
TBC68 | H0 | VH0 | M0 | L0 | TBC68 | J5 | Is there adequate protection of the intake point from livestock and wildlife? | TBC |  |  | 5 | TBC
TBC69 | H0 | VH0 | M0 | L0 | TBC69 | J6 | Does the availability of the water at the intake vary? | TBC |  |  | 3 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC69 | J7 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC69 | J8 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC69 | J9 |  | N/A | N/A
[6 empty] | Section K - SOURCE: Water Storage (prior to treatment) |  |  | H
TBC70 | H0 | VH0 | M0 | L0 | TBC70 | K1 | Is there a regular turn over of water? | TBC |  |  | 3 | TBC
TBC71 | H0 | VH0 | M0 | L0 | TBC71 | K2 | Are the storage tanks vulnerable to ingress, flooding or other microbial contamination (e.g. wildlife access)? | TBC |  |  | 4 | TBC
TBC72 | H0 | VH0 | M0 | L0 | TBC72 | K3 | Is there a stock-proof fence around any inspection chambers? | TBC |  |  | 4 | TBC
TBC73 | H0 | VH0 | M0 | L0 | TBC73 | K4 | Are the tanks regularly maintained to preserve their structural integrity and cleaned? | TBC |  |  | 4 | TBC
TBC74 | H0 | VH0 | M0 | L0 | TBC74 | K5 | Are the storage tanks adequately protected against vandalism? | TBC |  |  | 4 | TBC
TBC75 | H0 | VH0 | M0 | L0 | TBC75 | K6 | Is the cleaning regime for the tank appropriate? | TBC |  |  | 4 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC75 | K7 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC75 | K8 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC75 | K9 |  | N/A | N/A
[6 empty] | Section L - TREATMENT PLANT: Plant Design (i.e. excluding point of use devices in dwellings or premises) |  |  | H
TBC76 | H0 | VH0 | M0 | L0 | TBC76 | L1 | Is there adequate Cryptosporidium treatment in place? | TBC |  |  | 5 | TBC
TBC77 | H0 | VH0 | M0 | L0 | TBC77 | L2 | Is the treatment plant operating within the design capacity? | TBC |  |  | 5 | TBC
TBC78 | H0 | VH0 | M0 | L0 | TBC78 | L3 | Is it possible to by-pass any stage of treatment? | TBC |  |  | 5 | TBC
TBC79 | H0 | VH0 | M0 | L0 | TBC79 | L4 | Where there is a blending facility, is there an appropriate blending strategy? | TBC |  |  | 4 | TBC
TBC80 | H0 | VH0 | M0 | L0 | TBC80 | L5 | Are there frequent flow variations through the treatment plant, which render the treatment process inadequate? | TBC |  |  | 4 | TBC
TBC81 | H0 | VH0 | M0 | L0 | TBC81 | L6 | Are there frequent demand variations, which could cause insufficiency? | TBC |  |  | 3 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC81 | L7 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC81 | L8 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC81 | L9 |  | N/A | N/A
[6 empty] | Section M - TREATMENT PLANT: Filter beds (sand, anthracite, etc) |  |  | H
TBC82 | H0 | VH0 | M0 | L0 | TBC82 | M1 | Is there adequate pre-treatment (e.g. clarification) in place if required? | TBC |  |  | 5 | TBC
TBC83 | H0 | VH0 | M0 | L0 | TBC83 | M2 | Is there adequate process control for filtration (e.g. turbidity monitors)? | TBC |  |  | 5 | TBC
TBC84 | H0 | VH0 | M0 | L0 | TBC84 | M3 | Can the filters overload? | TBC |  |  | 5 | TBC
TBC85 | H0 | VH0 | M0 | L0 | TBC85 | M4 | Do the filters block? | TBC |  |  | 5 | TBC
TBC86 | H0 | VH0 | M0 | L0 | TBC86 | M5 | Is the media depth at a minimum to design specification? | TBC |  |  | 5 | TBC
TBC87 | H0 | VH0 | M0 | L0 | TBC87 | M6 | Is the filter media composition as per design specification? | TBC |  |  | 5 | TBC
TBC88 | H0 | VH0 | M0 | L0 | TBC88 | M7 | Is the backwashing regime operated to the design manual (including cycle length, uneven scour, pump failure, loss of filter media) | TBC |  |  | 5 | TBC
TBC89 | H0 | VH0 | M0 | L0 | TBC89 | M8 | Do the filters appear well maintained? | TBC |  |  | 5 | TBC
TBC90 | H0 | VH0 | M0 | L0 | TBC90 | M9 | Does the water run to waste when rapid gravity filters are started up? | TBC |  |  | 5 | TBC
TBC91 | H0 | VH0 | M0 | L0 | TBC91 | M10 | Can the filters be started up gradually (i.e. not immediately run at full capacity)? | TBC |  |  | 5 | TBC
TBC92 | H0 | VH0 | M0 | L0 | TBC92 | M11 | Where Cryptosporidium is potentially present in the raw water, is a turbidity of less than 1.0 NTU achieved in the filtered water? | TBC |  |  | 5 | TBC
TBC93 | H0 | VH0 | M0 | L0 | TBC93 | M12 | Is the backwash water recycled to head of works? | TBC |  |  | 5 | TBC
TBC94 | H0 | VH0 | M0 | L0 | TBC94 | M13 | Is algal growth apparent in/on filters? | TBC |  |  | 3 | TBC
TBC95 | H0 | VH0 | M0 | L0 | TBC95 | M14 | For slow sand filters, is the required ripening period adhered to before putting the water into supply? | TBC |  |  | 5 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC95 | M15 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC95 | M16 |  | N/A | N/A
[6 empty] | Section N - TREATMENT PLANT: Granular Activated Carbon (GAC) filters |  |  | H
TBC96 | H0 | VH0 | M0 | L0 | TBC96 | N1 | Has the GAC been installed as per the design specification? | TBC |  |  | 5 | TBC
TBC97 | H0 | VH0 | M0 | L0 | TBC97 | N2 | Is the GAC design appropriate for the nature of the raw water quality? | TBC |  |  | 5 | TBC
TBC98 | H0 | VH0 | M0 | L0 | TBC98 | N3 | Is the media depth and composition appropriate for the nature of the raw water quality? | TBC |  |  | 4 | TBC
TBC99 | H0 | VH0 | M0 | L0 | TBC99 | N4 | Is the plant regularly operated and maintained according to the design specification? | TBC |  |  | 4 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC99 | N5 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC99 | N6 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC99 | N7 |  | N/A | N/A
[6 empty] | Section O - TREATMENT PLANT: Ion Exchange (may be used for nitrate, arsenic or manganese removal etc.) |  |  | H
TBC100 | H0 | VH0 | M0 | L0 | TBC100 | O1 | Is the treatment plant operating within its design capacity? | TBC |  |  | 5 | TBC
TBC101 | H0 | VH0 | M0 | L0 | TBC101 | O2 | Is there adequate pre-treatment (e.g. filtration) in place if required? | TBC |  |  | 5 | TBC
TBC102 | H0 | VH0 | M0 | L0 | TBC102 | O3 | Is the media depth at a minimum to design specification? | TBC |  |  | 5 | TBC
TBC103 | H0 | VH0 | M0 | L0 | TBC103 | O4 | Is the ion exchange media composition as per design specification? | TBC |  |  | 5 | TBC
TBC104 | H0 | VH0 | M0 | L0 | TBC104 | O5 | Is there a suitable maintenance schedule? | TBC |  |  | 4 | TBC
TBC105 | H0 | VH0 | M0 | L0 | TBC105 | O6 | Is the regeneration regime as per design specification? | TBC |  |  | 5 | TBC
[6 empty] | Section P - TREATMENT PLANT: Other Filters |  |  | H
TBC106 | H0 | VH0 | M0 | L0 | TBC106 | P1 | Does the plant design take into account the raw water quality? | TBC |  |  | 5 | TBC
TBC107 | H0 | VH0 | M0 | L0 | TBC107 | P2 | Is there adequate pre-treatment to prevent membrane fouling and damage? | TBC |  |  | 5 | TBC
TBC108 | H0 | VH0 | M0 | L0 | TBC108 | P3 | Are the cleaning regimes (for descaling and antifouling, etc.) being followed as set out in the design specification? | TBC |  |  | 5 | TBC
TBC109 | H0 | VH0 | M0 | L0 | TBC109 | P4 | Are the chemicals used in the process as recommended by the manufacturer? | TBC |  |  | 5 | TBC
TBC110 | H0 | VH0 | M0 | L0 | TBC110 | P5 | Is there a procedure to confirm that the integrity of the membrane is maintained? | TBC |  |  | 5 | TBC
TBC111 | H0 | VH0 | M0 | L0 | TBC111 | P6 | Are the filters replaced as per the manufacturer's specifications (or more frequently)? | TBC |  |  | 5 | TBC
TBC112 | H0 | VH0 | M0 | L0 | TBC112 | P7 | Was the raw water quality taken into account when the filters were installed? | TBC |  |  | 5 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC112 | P8 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC112 | P9 |  | N/A | N/A
Section Q - TREATMENT: Desalination or Reverse Osmosis
TBC113 | H0 | VH0 | M0 | L0 | TBC113 | Q1 | Is there any likelihood of industrial, domestic or boating waste flows in the vicinity of the water intake to the desalination plant? | TBC |  |  | 5 | TBC
TBC114 | H0 | VH0 | M0 | L0 | TBC114 | Q2 | Could any chemical stores potentially contaminate the supply at the intake? | TBC |  |  | 4 | TBC
TBC115 | H0 | VH0 | M0 | L0 | TBC115 | Q3 | Are there variations in source water levels, which affect the ability to abstract water? | TBC |  |  | 3 | TBC
TBC116 | H0 | VH0 | M0 | L0 | TBC116 | Q4 | Is there adequate treatment to prevent membrane fouling and damage? | TBC |  |  | 4 | TBC
TBC117 | H0 | VH0 | M0 | L0 | TBC117 | Q5 | Are oxidants removed during pretreatment? | TBC |  |  | 3 | TBC
TBC118 | H0 | VH0 | M0 | L0 | TBC118 | Q6 | Has the operator mitigated against the demineralisation of the water? | TBC |  |  | 3 | TBC
TBC119 | H0 | VH0 | M0 | L0 | TBC119 | Q7 | Is the treated supply blended with other sources of drinking water in distribution? | TBC |  |  | 4 | TBC
TBC120 | H0 | VH0 | M0 | L0 | TBC120 | Q8 | Are the chemicals used in the process as recommended by the manufacturer? | TBC |  |  | 4 | TBC
TBC121 | H0 | VH0 | M0 | L0 | TBC121 | Q9 | Is the plant design appropriate for the nature of the raw water quality? | TBC |  |  | 5 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC121 | Q10 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC121 | Q11 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC121 | Q12 |  | N/A | N/A
[6 empty] | Section R - TREATMENT PLANT: Disinfection: UV |  |  | H
TBC122 | H0 | VH0 | M0 | L0 | TBC122 | R1 | Is there adequate preliminary treatment in place? | TBC |  |  | 5 | TBC
TBC123 | H0 | VH0 | M0 | L0 | TBC123 | R2 | Is there a validation certificate for the UV system? | TBC |  |  | 4 | TBC
TBC124 | H0 | VH0 | M0 | L0 | TBC124 | R3 | Can water be supplied if the U.V. is not operational? | TBC |  |  | 5 | TBC
TBC125 | H0 | VH0 | M0 | L0 | TBC125 | R4 | Is the UV operating within its validated range for the product type or lamp? | TBC |  |  | 5 | TBC
TBC126 | H0 | VH0 | M0 | L0 | TBC126 | R5 | Is the equipment regularly maintained e.g. bulb replacement, cleaning? | TBC |  |  | 5 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC126 | R6 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC126 | R7 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC126 | R8 |  | N/A | N/A
[6 empty] | Section S - TREATMENT PLANT: Disinfection: chlorination |  |  | H
TBC127 | H0 | VH0 | M0 | L0 | TBC127 | S1 | Is there a backup/standby system for automatic chlorine dosing or an automatic shutdown arrangement? | TBC |  |  | 5 | TBC
TBC128 | H0 | VH0 | M0 | L0 | TBC128 | S2 | Is there evidence that maintenance has been carried out of the disinfection system within the last 12 months? | TBC |  |  | 5 | TBC
TBC129 | H0 | VH0 | M0 | L0 | TBC129 | S3 | Is there an appropriate alarm in the event of loss of chlorine dosing? | TBC |  |  | 5 | TBC
TBC130 | H0 | VH0 | M0 | L0 | TBC130 | S4 | Are the chemicals of drinking water grade i.e. approved for use in drinking water supplies? | TBC |  |  | 3 | TBC
TBC131 | H0 | VH0 | M0 | L0 | TBC131 | S5 | Is the existing dosing effective? | TBC |  |  | 5 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC131 | S6 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC131 | S7 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC131 | S8 |  | N/A | N/A
[6 empty] | Section T - TREATMENT PLANT: Other (answer for any treatment process) |  |  | H
TBC132 | H0 | VH0 | M0 | L0 | TBC132 | T1 | Are all chemicals used for water treatment approved and in date? | TBC |  |  | 5 | TBC
TBC133 | H0 | VH0 | M0 | L0 | TBC133 | T2 | Are there controls in place for chemical deliveries to avoid chemicals being added to the wrong storage vessel? | TBC |  |  | 4 | TBC
TBC134 | H0 | VH0 | M0 | L0 | TBC134 | T3 | Are chemical injection point(s) protected against potential damage e.g. covered, frost proofing, etc? | TBC |  |  | 5 | TBC
TBC135 | H0 | VH0 | M0 | L0 | TBC135 | T4 | Are there procedures in place to ensure treatment is re-established after any loss of power supply? | TBC |  |  | 5 | TBC
TBC136 | H0 | VH0 | M0 | L0 | TBC136 | T5 | Is there a power back-up or alternative power supply? | TBC |  |  | 5 | TBC
TBC137 | H0 | VH0 | M0 | L0 | TBC137 | T6 | Is the treatment plant adequately protected against vandalism? | TBC |  |  | 5 | TBC
TBC138 | H0 | VH0 | M0 | L0 | TBC138 | T7 | Is the site liable to flooding which would result in loss or restriction of treatment process? | TBC |  |  | 5 | TBC
TBC139 | H0 | VH0 | M0 | L0 | TBC139 | T8 | Could access to the plant be lost or restricted due to weather extremes or other events? | TBC |  |  | 4 | TBC
TBC140 | H0 | VH0 | M0 | L0 | TBC140 | T9 | Could adverse weather conditions render the treatment process and/or chemicals ineffective? | TBC |  |  | 5 | TBC
TBC141 | H0 | VH0 | M0 | L0 | TBC141 | T10 | Are stored chemicals or oil adequately bunded? | TBC |  |  | 4 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC141 | T11 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC141 | T12 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC141 | T13 |  | N/A | N/A
[6 empty] | Section U - TREATMENT: Monitoring. Use this section for all treatment systems |  |  | H
TBC142 | H0 | VH0 | M0 | L0 | TBC142 | U1 | Are there appropriate online monitors? | TBC |  |  | 5 | TBC
TBC143 | H0 | VH0 | M0 | L0 | TBC143 | U2 | Are they calibrated and maintained? | TBC |  |  | 5 | TBC
TBC144 | H0 | VH0 | M0 | L0 | TBC144 | U3 | Do the on-line monitors have alarms? | TBC |  |  | 3 | TBC
TBC145 | H0 | VH0 | M0 | L0 | TBC145 | U4 | If monitors are not present on the supply, is any on-site testing being carried out? | TBC |  |  | 3 | TBC
TBC146 | H0 | VH0 | M0 | L0 | TBC146 | U5 | Is there a basic schematic for the treatment and monitoring equipment? | TBC |  |  | 3 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC146 | U6 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC146 | U7 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC146 | U8 |  | N/A | N/A
[6 empty] | Section V - DISTRIBUTION: Distribution Network |  |  | H
TBC147 | H0 | VH0 | M0 | L0 | TBC147 | V1 | After treatment is the water fully compliant with quality standards? | TBC |  |  | 5 | TBC
TBC148 | H0 | VH0 | M0 | L0 | TBC148 | V2 | Are there latrines, septic tanks, waste pipes, animal enclosures or cess pits present in the vicinity of the distribution system? | TBC |  |  | 5 | TBC
TBC149 | H0 | VH0 | M0 | L0 | TBC149 | V3 | Is there evidence of disinfection by-products in the network (e.g. taste problems due to THM's)? | TBC |  |  | 4 | TBC
TBC150 | H0 | VH0 | M0 | L0 | TBC150 | V4 | If chlorine disinfection is practiced is there a disinfectant residual in the distribution network? | TBC |  |  | 3 | TBC
TBC151 | H0 | VH0 | M0 | L0 | TBC151 | V5 | Is there a suitable written procedure for mains repair and maintenance? | TBC |  |  | 5 | TBC
TBC152 | H0 | VH0 | M0 | L0 | TBC152 | V6 | Is there history of any fractures or faults in the distribution system which could allow ingress of contamination? | TBC |  |  | 4 | TBC
TBC153 | H0 | VH0 | M0 | L0 | TBC153 | V7 | Is there any other route by which contamination can enter the distribution network via back-flow? If there is ponding of surface water or poor drainage, could water be pulled into the system during low pressure or changes in pressure, e.g. backflow from hoses, taps, or standpipes? | TBC |  |  | 4 | TBC
TBC154 | H0 | VH0 | M0 | L0 | TBC154 | V8 | Is there evidence any pipes are coal tar lined? | TBC |  |  | 4 | TBC
TBC155 | H0 | VH0 | M0 | L0 | TBC155 | V9 | Do any third parties have access to hydrants or other points in the distribution system? | TBC |  |  | 5 | TBC
TBC156 | H0 | VH0 | M0 | L0 | TBC156 | V10 | Is there potential contamination of plastic pipes through designated contaminated land, oil from generators/household fuel tanks/fuel stores or solvent spillage? | TBC |  |  | 4 | TBC
TBC157 | H0 | VH0 | M0 | L0 | TBC157 | V11 | Are there any pipes exposed and at risk of damage by any means e.g. vermin, vehicle, UV/sunlight damage, overheating or freezing? | TBC |  |  | 4 | TBC
TBC158 | H0 | VH0 | M0 | L0 | TBC158 | V12 | If there are valves in the network which are normally closed, are there measures in place to control when and how they are operated? | TBC |  |  | 2 | TBC
TBC159 | H0 | VH0 | M0 | L0 | TBC159 | V13 | Are there sections of pipework containing stagnant water? | TBC |  |  | 2 | TBC
TBC160 | H0 | VH0 | M0 | L0 | TBC160 | V14 | Where there is copper pipework present, is it corroding? | TBC |  |  | 3 | TBC
TBC161 | H0 | VH0 | M0 | L0 | TBC161 | V15 | Is there the potential for backflow from commercial premises, domestic premises, unauthorised connections, standpipes or unregulated supplies? | TBC |  |  | 5 | TBC
TBC162 | H0 | VH0 | M0 | L0 | TBC162 | V16 | Are lead pipes present in the supply? | TBC |  |  | 4 | TBC
TBC163 | H0 | VH0 | M0 | L0 | TBC163 | V17 | Do all junctions in the supply network, particularly animal watering systems and standpipes, have backflow protection? | TBC |  |  | 5 | TBC
TBC164 | H0 | VH0 | M0 | L0 | TBC164 | V18 | Are there any known or potential cross-connections (between different sources, greywater systems, sewage pipes or other waste pipes)? | TBC |  |  | 5 | TBC
TBC165 | H0 | VH0 | M0 | L0 | TBC165 | V19 | Have there been complaints or reports of water quality problems (e.g. taste, odours or reports of any aquatic animals (freshwater shrimp, louse or worms)? | TBC |  |  | 3 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC165 | V20 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC165 | V21 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC165 | V22 |  | N/A | N/A
[6 empty] | Section W - DISTRIBUTION: Storage of treated water in the distribution network (including private distribution systems) |  |  | H
TBC166 | H0 | VH0 | M0 | L0 | TBC166 | W1 | Are all treated water reservoirs covered appropriately e.g. No risk of ingress and/or constructed of suitable material? | TBC |  |  | 4 | TBC
TBC167 | H0 | VH0 | M0 | L0 | TBC167 | W2 | Are all treated water reservoirs of sufficient structural integrity to prevent ingress of contamination, including covers? | TBC |  |  | 4 | TBC
TBC168 | H0 | VH0 | M0 | L0 | TBC168 | W3 | Is the integrity of the reservoir suitably robust against damage by weather or animals? | TBC |  |  | 4 | TBC
TBC169 | H0 | VH0 | M0 | L0 | TBC169 | W4 | Are there any waste water pipes, or waste water storage tanks adjacent to the tanks/reservoirs? | TBC |  |  | 4 | TBC
TBC170 | H0 | VH0 | M0 | L0 | TBC170 | W5 | Are there any unprotected or inadequately protected access covers and/or vents? | TBC |  |  | 4 | TBC
TBC171 | H0 | VH0 | M0 | L0 | TBC171 | W6 | Are any treated water reservoirs adequately protected against solar heat gain, vandalism (deliberate contamination of treated water and unauthorised access)? | TBC |  |  | 4 | TBC
TBC172 | H0 | VH0 | M0 | L0 | TBC172 | W7 | Is there a stock-proof fence around any inspection chambers? | TBC |  |  | 4 | TBC
TBC173 | H0 | VH0 | M0 | L0 | TBC173 | W8 | Are the reservoirs regularly maintained and cleaned with appropriate records? | TBC |  |  | 4 | TBC
TBC174 | H0 | VH0 | M0 | L0 | TBC174 | W9 | Is there a regular turn over of water, such that the capacity of the storage vessel matches demand? | TBC |  |  | 3 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC174 | W10 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC174 | W11 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC174 | W12 |  | N/A | N/A
[6 empty] | Section X - Premises supplied (applicable to domestic dwelling or commercial premises) |  |  | H
TBC175 | H0 | VH0 | M0 | L0 | TBC175 | X1 | Is the drinking water supply to any customer premises (kitchen tap) supplied via a loft tank? Note; there is no need to inspect loft tanks, just ask for evidence. If no, move on to question X4. | TBC |  |  | 5 | TBC
TBC176 | H0 | VH0 | M0 | L0 | TBC176 | X2 | If yes, do all loft tanks have a robust vermin proof cover? | TBC |  |  | 4 | TBC
TBC177 | H0 | VH0 | M0 | L0 | TBC177 | X3 | If yes, is there evidence the loft tanks are cleaned at least once per year? | TBC |  |  | 3 | TBC
TBC178 | H0 | VH0 | M0 | L0 | TBC178 | X4 | Is there any lead pipe work within the properties? | TBC |  |  | 4 | TBC
TBC179 | H0 | VH0 | M0 | L0 | TBC179 | X5 | Is the water at the consumers tap clear, taste and odour-free? | TBC |  |  | 2 | TBC
TBC180 | H0 | VH0 | M0 | L0 | TBC180 | X6 | Is there adequate backflow protection for any rainwater harvesting systems in place at any of the properties? | TBC |  |  | 5 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC180 | X7 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC180 | X8 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC180 | X9 |  | N/A | N/A
[6 empty] | Section Y - Point of use devices ( i.e individual property treatment systems such as UV systems, filter, membrane, Reverse osmosis (RO) under the sink) |  |  | H
TBC181 | H0 | VH0 | M0 | L0 | TBC181 | Y1 | Is the treatment system maintained to the manufacturer's instructions (filter changeover, cleaning)? | TBC |  |  | 5 | TBC
TBC182 | H0 | VH0 | M0 | L0 | TBC182 | Y2 | Is the design of the individual treatment system appropriate for the nature of the raw water quality? | TBC |  |  | 5 | TBC
FALSE | H0 | VH0 | M0 | L0 | TBC182 | Y3 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC182 | Y4 |  | N/A | N/A
FALSE | H0 | VH0 | M0 | L0 | TBC182 | Y5 |  | N/A | N/A
[6 empty] | Section Z - MANAGEMENT & CONTROL: To determine the risk rating for this section, answer questions Z2 to Z27 to inform the answer to Z1.There should only one risk rating for this section in Z1. |  |  | H
TBC183 | H0 | VH0 | M0 | L0 | TBC183 | Z1 | CONFIDENCE IN MANAGEMENT? To determine the risk rating for this section, answer questions Z2 to Z27 to inform the answer to Z1.There should only one risk rating for this section in Z1. | TBC |  |  | 5 | TBC
TBC184 | H0 | VH0 | M0 | L0 | TBC184 | Z2 | Are records kept of key checks e.g. Equipment maintenance, site inspections, on-site tests, etc | TBC |  |  |  | TBC
TBC185 | H0 | VH0 | M0 | L0 | TBC185 | Z3 | Are there written procedures for the operation and maintenance of equipment? | TBC |  |  |  | TBC
TBC186 | H0 | VH0 | M0 | L0 | TBC186 | Z4 | Are there procedures for responding to alarms, monitors, on-site tests? | TBC |  |  |  | TBC
TBC187 | H0 | VH0 | M0 | L0 | TBC187 | Z5 | Is there a written procedure for installations, pipe repairs and maintenance to protect against microbial contamination? | TBC |  |  |  | TBC
TBC188 | H0 | VH0 | M0 | L0 | TBC188 | Z6 | Do operators have adequate (even if informal) general hygiene awareness? | TBC |  |  |  | TBC
TBC189 | H0 | VH0 | M0 | L0 | TBC189 | Z7 | Is there a documented procedure for operation of valves including authorisation? | TBC |  |  |  | TBC
TBC190 | H0 | VH0 | M0 | L0 | TBC190 | Z8 | Are there any records of reservoir cleaning and maintenance? | TBC |  |  |  | TBC
TBC191 | H0 | VH0 | M0 | L0 | TBC191 | Z9 | Are the records checked to ensure the required maintenance and checks have been carried out satisfactorily? | TBC |  |  |  | TBC
TBC192 | H0 | VH0 | M0 | L0 | TBC192 | Z10 | Is there a stock control process for any chemicals used to ensure their continuous availability? | TBC |  |  |  | TBC
TBC193 | H0 | VH0 | M0 | L0 | TBC193 | Z11 | Is there a stock control process for any key spare parts/equipment? | TBC |  |  |  | TBC
TBC194 | H0 | VH0 | M0 | L0 | TBC194 | Z12 | Is there a documented contingency plan in the event of power failure, equipment failure? | TBC |  |  |  | TBC
TBC195 | H0 | VH0 | M0 | L0 | TBC195 | Z13 | Is the person nominated to manage the supply trained to run and maintain the supply? | TBC |  |  |  | TBC
TBC196 | H0 | VH0 | M0 | L0 | TBC196 | Z14 | Is there a nominated person to run the supply when the above person is unavailable? | TBC |  |  |  | TBC
TBC197 | H0 | VH0 | M0 | L0 | TBC197 | Z15 | Is there a documented system to report emergencies to management/owner of supply? | TBC |  |  |  | TBC
TBC198 | H0 | VH0 | M0 | L0 | TBC198 | Z16 | Are there calibration schedules in place for key dosing and monitoring equipment? | TBC |  |  |  | TBC
TBC199 | H0 | VH0 | M0 | L0 | TBC199 | Z17 | Is there a weekly site inspection to check for changes (e.g. Dead sheep, broken fence)? | TBC |  |  |  | TBC
TBC200 | H0 | VH0 | M0 | L0 | TBC200 | Z18 | Are there appropriate procedures for rectifying customer complaints? | TBC |  |  |  | TBC
TBC201 | H0 | VH0 | M0 | L0 | TBC201 | Z19 | Are there procedures and records in place to inform the LA of any changes to the risk assessment? | TBC |  |  |  | TBC
TBC202 | H0 | VH0 | M0 | L0 | TBC202 | Z20 | If a risk assessment has previously been carried out, is there a plan for delivering the required improvements? | TBC |  |  |  | TBC
TBC203 | H0 | VH0 | M0 | L0 | TBC203 | Z21 | Is there a detailed plan of the site including details of source, tanks, distribution pipes, valves (material, age) etc. | TBC |  |  |  | TBC
TBC204 | H0 | VH0 | M0 | L0 | TBC204 | Z22 | Is there a documented contingency for the supply running out? | TBC |  |  |  | TBC
TBC205 | H0 | VH0 | M0 | L0 | TBC205 | Z23 | Do the treatment chemicals and materials conform to Regulation 5? Have all new installations since 2010 complied with Regulation 5 (or equivalent in Wales) – products and processes | TBC |  |  |  | TBC
TBC206 | H0 | VH0 | M0 | L0 | TBC206 | Z24 | Do all materials involved in the distribution system conform to Regulation 5? Have all new installations since 2010 complied with Regulation 5 (or equivalent in Wales) – products and processes? | TBC |  |  |  | TBC
TBC207 | H0 | VH0 | M0 | L0 | TBC207 | Z25 | Is there a documented procedure for carrying out mains tappings (making new connections into pipes)? | TBC |  |  |  | TBC
TBC208 | H0 | VH0 | M0 | L0 | TBC208 | Z26 | Are persons carrying out this work competent and trained in this procedure?(e.g. approved by a water company or part of the Water Safe Scheme)? | TBC |  |  |  | TBC
TBC209 | H0 | VH0 | M0 | L0 | TBC209 | Z27 | Any additional site specific hazard(s) associated with management | TBC |  |  |  | TBC

## Unanswered_Questions
Private Water Supply: Risk Assessment Tool This sheet may be printed and taken to site to use as a guide and a reminder sheet for questions to ask following your desktop study. Any questions already answered will not appear, however any comments for reminders and notes you put in on the risk assessment tab will appear here for reference.
TBC | Local Authority: Supply Reference:
Supply Name & Address:
Risk No. | Unanswered question | Likelihood | Severity | Comments
A0 | Have there been any changes since risk assessment last carried out? |  |  | 0 | TBC1 | 1
A1 | Is there a site plan and/or schematic showing location of source, chambers, tanks, distribution network including valves, pipes, consumer premises etc.? |  |  | 0 | TBC2 | 2
A2 | Are there any procedures and/or written records for the supply (i.e. for checks, monitoring or maintenance, etc.)? |  |  | 0 | TBC3 | 3
A3 | Are there any manufacturers' instructions for the equipment on the supply? |  |  | 0 | TBC4 | 4
A4 | Is there an emergency plan for the provision of an alternative water supply? |  |  | 0 | TBC5 | 5
A5 | Has the owner or operators had appropriate training for the supply? |  |  | 0 | TBC6 | 6
A6 | Does the sampling history identify the presence of any hazards? |  |  | 0 | TBC7 | 7
B1 | Are there latrines, septic tanks, animal enclosures or cess pits present within 50m of the source? |  |  | 0 | TBC8 | 8
B2 | Are there any waste pipes (sewage) adjacent to the source? |  |  | 0 | TBC9 | 9
B3 | Is there a risk of microbial contamination (from slurry spreading, and/or storage of slurry or dung)? |  |  | 0 | TBC10 | 10
B4 | Is there a risk of pesticides or chemical contamination (e.g. sheep dipping chemicals) |  |  | 0 | TBC11 | 11
B5 | Are chemical fertilisers used? |  |  | 0 | TBC12 | 12
B6 | Is there history of mining in the catchment (i.e. chemical or metal contamination)? |  |  | 0 | TBC13 | 13
B7 | Does the local geology suggest the present of - boron, arsenic, lead, fluoride, uranium, nickel, radon or other potentially harmful natural substance in raw water? |  |  | 0 | TBC14 | 14
B8 | Is the source likely to be affected by any contaminated land including landfill sites in the catchment? |  |  | 0 | TBC15 | 15
B9 | Is there a likelihood of insufficiency of supply i.e. over-abstraction of source or during drought conditions |  |  | 0 | TBC16 | 16
B10 | Is the source adequately protected against vandalism (deliberate contamination of source and unauthorised access)? |  |  | 0 | TBC17 | 17
B11 | Is there a risk of oil spill entering the supply (e.g. generators, household heating oil, farm fuel, generators, road traffic accident or the presence of a redundant tanker etc.)? |  |  | 0 | TBC18 | 18
B15 | Are there any man made sources of tritium in the catchment which could affect the water supply? |  |  | 0 | TBC19 | 19
B16 | Has the Environment Agency any record of historic pollution event(s) in the catchment which contained radioactive substances? |  |  | 0 | TBC20 | 20
B17 | Does the local water company have a notice allowing them to cease monitoring for tritium or ID for abstraction points from the same aquifer? |  |  | 0 | TBC21 | 21
B18 | Is there any monitoring data (EA/Wco/LA) for radioactive substances in this supply or another supply in the same water body indicating levels above the standard/value? |  |  | 0 | TBC22 | 22
B19 | Does the ‘Radioactivity in Food and the environment’ report indicate the likely presence of radioactive substances? |  |  | 0 | TBC23 | 23
B20 | If gross alpha or gross beta exceed the limit, does the Indicative Dose (ID)calculation confirm the value is <0.1mSv? |  |  | 0 | TBC24 | 24
C1 | Is there a noticeable change in the appearance of the water from time to time (colour, cloudiness/turbidity)? |  |  | 0 | TBC25 | 25
C2 | Is the source exposed to risks of faecal contamination from wildlife (this will always be yes for all surface water sources, i.e. rivers, lakes and streams)? |  |  | 0 | TBC26 | 26
C3 | Is there waste-water discharging biological matter into the source? |  |  | 0 | TBC27 | 27
C4 | Is there waste-water discharging chemical substances into the source? |  |  | 0 | TBC28 | 28
C5 | Are there unbunded stores of farm waste or silage in the catchment? |  |  | 0 | TBC29 | 29
C6 | Is local forestry activity causing or likely to cause suspended particles in the source water? |  |  | 0 | TBC30 | 30
C7 | Is freshwater aquaculture practised upstream, causing contamination (feed, pesticides etc.)? |  |  | 0 | TBC31 | 31
C8 | Is there run off from construction/development activities upstream of intake causing contamination (oil spills, silt, cement, bentonites, soakaways, open tanks, surface water inceptors)? |  |  | 0 | TBC32 | 32
C9 | Is local quarrying activity causing or likely to cause suspended particles or any chemicals in the source water? |  |  | 0 | TBC33 | 33
C10 | Is the source water used for recreational purposes? |  |  | 0 | TBC34 | 34
C11 | Is the source water subject to seasonal algal blooms including toxin producing algae (cyanobacteria)? |  |  | 0 | TBC35 | 35
C12 | Is the spring chamber designed and constructed to exclude surface water or spillages of contaminated material causing microbial or other contamination (through the cover or the lining) and is it in a satisfactory state of repair? |  |  | 0 | TBC36 | 36
C13 | Does the spring chamber extend at least 150mm above the level of the floor with an apron sloping away from a secure cover? |  |  | 0 | TBC37 | 37
D1 | Where there are abandoned wells or observation boreholes are they adequately capped, fenced and protected? |  |  | 0 | TBC38 | 38
D2 | Are livestock excluded from the vicinity of the headworks (e.g. by fencing) to minimise the risk of microbial contamination? |  |  | 0 | TBC39 | 39
D3 | Is there evidence of standing water/ponding within 50m of the headworks? |  |  | 0 | TBC40 | 40
D4 | Is the borehole or well appropriately lined with casing and grouted to prevent ingress of shallow subsurface and/or surface water? |  |  | 0 | TBC41 | 41
D5 | If a chamber is present does it have barrier(s) to prevent ingress of surface water through the walls/floor (grouting/diversion ditch/walls etc.)? |  |  | 0 | TBC42 | 42
D6 | If a chamber is present does it have a cover that is non-degradable material that would prevent ingress of rainwater, vermin and is lockable (if not inside a locked building)? |  |  | 0 | TBC43 | 43
D7 | Are the headworks completely sealed so that no surface water, spillages or vermin/insects can enter? |  |  | 0 | TBC44 | 44
D8 | Are there land drains which channel water into the source? |  |  | 0 | TBC45 | 45
D9 | Are there historic results from the supply confirming the radon levels are below 100Bq/l? |  |  | 0 | TBC46 | 46
D10 | Does the local water company have a waiver for radon for abstraction points in the same aquifer? |  |  | 0 | TBC47 | 47
D11 | Do radon-in-air measurements confirm the levels are below 200Bq/m3 (where there is no existing radon treatment)? |  |  | 0 | TBC48 | 48
D12 | Does the PHE report or AEA Ricardo report identify the site as moderate or high hazards rating? |  |  | 0 | TBC49 | 49
D13 | Do sample results indicate radon levels are greater than 1000Bq/l? |  |  | 0 | TBC50 | 50
D14 | Is the source exposed to risks of faecal contamination from wildlife |  |  | 0 | TBC51 | 51
E1 | Is there evidence the supply main is coal tar lined? |  |  | 0 | TBC52 | 52
E2 | Are there sediments in the main? |  |  | 0 | TBC53 | 53
E3 | Is the section of main upstream of the point of supply subject to good turnover of water (e.g. are there connections to properties nearby which would ensure the water is refreshed in the main constantly)? |  |  | 0 | TBC54 | 54
E4 | If the area feeding the supply has had water quality related complaints in the last 12 months, have the causes been mitigated? |  |  | 0 | TBC55 | 55
E5 | Have any chemical parameters exceeded the standard in the previous 12 months in the mains supply? |  |  | 0 | TBC56 | 56
E6 | Are there backflow protection deficiencies at any upstream industrial or commercial premises? |  |  | 0 | TBC57 | 57
I1 | Is there any protection against faecal or chemical contamination e.g. from wildlife or industrial emissions? |  |  | 0 | TBC58 | 58
I2 | Are there any screens to prevent material entering the collection chamber (e.g. leaves, insects, twigs)? |  |  | 0 | TBC59 | 59
I3 | Are there any trees overhanging the roof? |  |  | 0 | TBC60 | 60
I4 | Is there evidence of lead, tin, copper, asphalt, new galvanised sheeting or wood preservatives on the roof? |  |  | 0 | TBC61 | 61
I5 | Is there a bypass mechanism to exclude the first flush of rainwater from the roof? |  |  | 0 | TBC62 | 62
I6 | Is there adequate backflow protection for any rainwater harvesting systems in place at any of the properties? |  |  | 0 | TBC63 | 63
J1 | Does the water quality vary at the intake point due to streaming/stratification/algal blooms/increased turbidity? |  |  | 0 | TBC64 | 64
J2 | Are there screens in place at the intake? |  |  | 0 | TBC65 | 65
J3 | Where screens are present, is there a mechanism to remove debris? |  |  | 0 | TBC66 | 66
J4 | Does sediment build up inside the chamber and pipework after the intake point? |  |  | 0 | TBC67 | 67
J5 | Is there adequate protection of the intake point from livestock and wildlife? |  |  | 0 | TBC68 | 68
J6 | Does the availability of the water at the intake vary? |  |  | 0 | TBC69 | 69
K1 | Is there a regular turn over of water? |  |  | 0 | TBC70 | 70
K2 | Are the storage tanks vulnerable to ingress, flooding or other microbial contamination (e.g. wildlife access)? |  |  | 0 | TBC71 | 71
K3 | Is there a stock-proof fence around any inspection chambers? |  |  | 0 | TBC72 | 72
K4 | Are the tanks regularly maintained to preserve their structural integrity and cleaned? |  |  | 0 | TBC73 | 73
K5 | Are the storage tanks adequately protected against vandalism? |  |  | 0 | TBC74 | 74
K6 | Is the cleaning regime for the tank appropriate? |  |  | 0 | TBC75 | 75
L1 | Is there adequate Cryptosporidium treatment in place? |  |  | 0 | TBC76 | 76
L2 | Is the treatment plant operating within the design capacity? |  |  | 0 | TBC77 | 77
L3 | Is it possible to by-pass any stage of treatment? |  |  | 0 | TBC78 | 78
L4 | Where there is a blending facility, is there an appropriate blending strategy? |  |  | 0 | TBC79 | 79
L5 | Are there frequent flow variations through the treatment plant, which render the treatment process inadequate? |  |  | 0 | TBC80 | 80
L6 | Are there frequent demand variations, which could cause insufficiency? |  |  | 0 | TBC81 | 81
M1 | Is there adequate pre-treatment (e.g. clarification) in place if required? |  |  | 0 | TBC82 | 82
M2 | Is there adequate process control for filtration (e.g. turbidity monitors)? |  |  | 0 | TBC83 | 83
M3 | Can the filters overload? |  |  | 0 | TBC84 | 84
M4 | Do the filters block? |  |  | 0 | TBC85 | 85
M5 | Is the media depth at a minimum to design specification? |  |  | 0 | TBC86 | 86
M6 | Is the filter media composition as per design specification? |  |  | 0 | TBC87 | 87
M7 | Is the backwashing regime operated to the design manual (including cycle length, uneven scour, pump failure, loss of filter media) |  |  | 0 | TBC88 | 88
M8 | Do the filters appear well maintained? |  |  | 0 | TBC89 | 89
M9 | Does the water run to waste when rapid gravity filters are started up? |  |  | 0 | TBC90 | 90
M10 | Can the filters be started up gradually (i.e. not immediately run at full capacity)? |  |  | 0 | TBC91 | 91
M11 | Where Cryptosporidium is potentially present in the raw water, is a turbidity of less than 1.0 NTU achieved in the filtered water? |  |  | 0 | TBC92 | 92
M12 | Is the backwash water recycled to head of works? |  |  | 0 | TBC93 | 93
M13 | Is algal growth apparent in/on filters? |  |  | 0 | TBC94 | 94
M14 | For slow sand filters, is the required ripening period adhered to before putting the water into supply? |  |  | 0 | TBC95 | 95
N1 | Has the GAC been installed as per the design specification? |  |  | 0 | TBC96 | 96
N2 | Is the GAC design appropriate for the nature of the raw water quality? |  |  | 0 | TBC97 | 97
N3 | Is the media depth and composition appropriate for the nature of the raw water quality? |  |  | 0 | TBC98 | 98
N4 | Is the plant regularly operated and maintained according to the design specification? |  |  | 0 | TBC99 | 99
O1 | Is the treatment plant operating within its design capacity? |  |  | 0 | TBC100 | 100
O2 | Is there adequate pre-treatment (e.g. filtration) in place if required? |  |  | 0 | TBC101 | 101
O3 | Is the media depth at a minimum to design specification? |  |  | 0 | TBC102 | 102
O4 | Is the ion exchange media composition as per design specification? |  |  | 0 | TBC103 | 103
O5 | Is there a suitable maintenance schedule? |  |  | 0 | TBC104 | 104
O6 | Is the regeneration regime as per design specification? |  |  | 0 | TBC105 | 105
P1 | Does the plant design take into account the raw water quality? |  |  | 0 | TBC106 | 106
P2 | Is there adequate pre-treatment to prevent membrane fouling and damage? |  |  | 0 | TBC107 | 107
P3 | Are the cleaning regimes (for descaling and antifouling, etc.) being followed as set out in the design specification? |  |  | 0 | TBC108 | 108
P4 | Are the chemicals used in the process as recommended by the manufacturer? |  |  | 0 | TBC109 | 109
P5 | Is there a procedure to confirm that the integrity of the membrane is maintained? |  |  | 0 | TBC110 | 110
P6 | Are the filters replaced as per the manufacturer's specifications (or more frequently)? |  |  | 0 | TBC111 | 111
P7 | Was the raw water quality taken into account when the filters were installed? |  |  | 0 | TBC112 | 112
Q1 | Is there any likelihood of industrial, domestic or boating waste flows in the vicinity of the water intake to the desalination plant? |  |  | 0 | TBC113 | 113
Q2 | Could any chemical stores potentially contaminate the supply at the intake? |  |  | 0 | TBC114 | 114
Q3 | Are there variations in source water levels, which affect the ability to abstract water? |  |  | 0 | TBC115 | 115
Q4 | Is there adequate treatment to prevent membrane fouling and damage? |  |  | 0 | TBC116 | 116
Q5 | Are oxidants removed during pretreatment? |  |  | 0 | TBC117 | 117
Q6 | Has the operator mitigated against the demineralisation of the water? |  |  | 0 | TBC118 | 118
Q7 | Is the treated supply blended with other sources of drinking water in distribution? |  |  | 0 | TBC119 | 119
Q8 | Are the chemicals used in the process as recommended by the manufacturer? |  |  | 0 | TBC120 | 120
Q9 | Is the plant design appropriate for the nature of the raw water quality? |  |  | 0 | TBC121 | 121
R1 | Is there adequate preliminary treatment in place? |  |  | 0 | TBC122 | 122
R2 | Is there a validation certificate for the UV system? |  |  | 0 | TBC123 | 123
R3 | Can water be supplied if the U.V. is not operational? |  |  | 0 | TBC124 | 124
R4 | Is the UV operating within its validated range for the product type or lamp? |  |  | 0 | TBC125 | 125
R5 | Is the equipment regularly maintained e.g. bulb replacement, cleaning? |  |  | 0 | TBC126 | 126
S1 | Is there a backup/standby system for automatic chlorine dosing or an automatic shutdown arrangement? |  |  | 0 | TBC127 | 127
S2 | Is there evidence that maintenance has been carried out of the disinfection system within the last 12 months? |  |  | 0 | TBC128 | 128
S3 | Is there an appropriate alarm in the event of loss of chlorine dosing? |  |  | 0 | TBC129 | 129
S4 | Are the chemicals of drinking water grade i.e. approved for use in drinking water supplies? |  |  | 0 | TBC130 | 130
S5 | Is the existing dosing effective? |  |  | 0 | TBC131 | 131
T1 | Are all chemicals used for water treatment approved and in date? |  |  | 0 | TBC132 | 132
T2 | Are there controls in place for chemical deliveries to avoid chemicals being added to the wrong storage vessel? |  |  | 0 | TBC133 | 133
T3 | Are chemical injection point(s) protected against potential damage e.g. covered, frost proofing, etc? |  |  | 0 | TBC134 | 134
T4 | Are there procedures in place to ensure treatment is re-established after any loss of power supply? |  |  | 0 | TBC135 | 135
T5 | Is there a power back-up or alternative power supply? |  |  | 0 | TBC136 | 136
T6 | Is the treatment plant adequately protected against vandalism? |  |  | 0 | TBC137 | 137
T7 | Is the site liable to flooding which would result in loss or restriction of treatment process? |  |  | 0 | TBC138 | 138
T8 | Could access to the plant be lost or restricted due to weather extremes or other events? |  |  | 0 | TBC139 | 139
T9 | Could adverse weather conditions render the treatment process and/or chemicals ineffective? |  |  | 0 | TBC140 | 140
T10 | Are stored chemicals or oil adequately bunded? |  |  | 0 | TBC141 | 141
U1 | Are there appropriate online monitors? |  |  | 0 | TBC142 | 142
U2 | Are they calibrated and maintained? |  |  | 0 | TBC143 | 143
U3 | Do the on-line monitors have alarms? |  |  | 0 | TBC144 | 144
U4 | If monitors are not present on the supply, is any on-site testing being carried out? |  |  | 0 | TBC145 | 145
U5 | Is there a basic schematic for the treatment and monitoring equipment? |  |  | 0 | TBC146 | 146
V1 | After treatment is the water fully compliant with quality standards? |  |  | 0 | TBC147 | 147
V2 | Are there latrines, septic tanks, waste pipes, animal enclosures or cess pits present in the vicinity of the distribution system? |  |  | 0 | TBC148 | 148
V3 | Is there evidence of disinfection by-products in the network (e.g. taste problems due to THM's)? |  |  | 0 | TBC149 | 149
V4 | If chlorine disinfection is practiced is there a disinfectant residual in the distribution network? |  |  | 0 | TBC150 | 150
V5 | Is there a suitable written procedure for mains repair and maintenance? |  |  | 0 | TBC151 | 151
V6 | Is there history of any fractures or faults in the distribution system which could allow ingress of contamination? |  |  | 0 | TBC152 | 152
V7 | Is there any other route by which contamination can enter the distribution network via back-flow? If there is ponding of surface water or poor drainage, could water be pulled into the system during low pressure or changes in pressure, e.g. backflow from hoses, taps, or standpipes? |  |  | 0 | TBC153 | 153
V8 | Is there evidence any pipes are coal tar lined? |  |  | 0 | TBC154 | 154
V9 | Do any third parties have access to hydrants or other points in the distribution system? |  |  | 0 | TBC155 | 155
V10 | Is there potential contamination of plastic pipes through designated contaminated land, oil from generators/household fuel tanks/fuel stores or solvent spillage? |  |  | 0 | TBC156 | 156
V11 | Are there any pipes exposed and at risk of damage by any means e.g. vermin, vehicle, UV/sunlight damage, overheating or freezing? |  |  | 0 | TBC157 | 157
V12 | If there are valves in the network which are normally closed, are there measures in place to control when and how they are operated? |  |  | 0 | TBC158 | 158
V13 | Are there sections of pipework containing stagnant water? |  |  | 0 | TBC159 | 159
V14 | Where there is copper pipework present, is it corroding? |  |  | 0 | TBC160 | 160
V15 | Is there the potential for backflow from commercial premises, domestic premises, unauthorised connections, standpipes or unregulated supplies? |  |  | 0 | TBC161 | 161
V16 | Are lead pipes present in the supply? |  |  | 0 | TBC162 | 162
V17 | Do all junctions in the supply network, particularly animal watering systems and standpipes, have backflow protection? |  |  | 0 | TBC163 | 163
V18 | Are there any known or potential cross-connections (between different sources, greywater systems, sewage pipes or other waste pipes)? |  |  | 0 | TBC164 | 164
V19 | Have there been complaints or reports of water quality problems (e.g. taste, odours or reports of any aquatic animals (freshwater shrimp, louse or worms)? |  |  | 0 | TBC165 | 165
W1 | Are all treated water reservoirs covered appropriately e.g. No risk of ingress and/or constructed of suitable material? |  |  | 0 | TBC166 | 166
W2 | Are all treated water reservoirs of sufficient structural integrity to prevent ingress of contamination, including covers? |  |  | 0 | TBC167 | 167
W3 | Is the integrity of the reservoir suitably robust against damage by weather or animals? |  |  | 0 | TBC168 | 168
W4 | Are there any waste water pipes, or waste water storage tanks adjacent to the tanks/reservoirs? |  |  | 0 | TBC169 | 169
W5 | Are there any unprotected or inadequately protected access covers and/or vents? |  |  | 0 | TBC170 | 170
W6 | Are any treated water reservoirs adequately protected against solar heat gain, vandalism (deliberate contamination of treated water and unauthorised access)? |  |  | 0 | TBC171 | 171
W7 | Is there a stock-proof fence around any inspection chambers? |  |  | 0 | TBC172 | 172
W8 | Are the reservoirs regularly maintained and cleaned with appropriate records? |  |  | 0 | TBC173 | 173
W9 | Is there a regular turn over of water, such that the capacity of the storage vessel matches demand? |  |  | 0 | TBC174 | 174
X1 | Is the drinking water supply to any customer premises (kitchen tap) supplied via a loft tank? Note; there is no need to inspect loft tanks, just ask for evidence. If no, move on to question X4. |  |  | 0 | TBC175 | 175
X2 | If yes, do all loft tanks have a robust vermin proof cover? |  |  | 0 | TBC176 | 176
X3 | If yes, is there evidence the loft tanks are cleaned at least once per year? |  |  | 0 | TBC177 | 177
X4 | Is there any lead pipe work within the properties? |  |  | 0 | TBC178 | 178
X5 | Is the water at the consumers tap clear, taste and odour-free? |  |  | 0 | TBC179 | 179
X6 | Is there adequate backflow protection for any rainwater harvesting systems in place at any of the properties? |  |  | 0 | TBC180 | 180
Y1 | Is the treatment system maintained to the manufacturer's instructions (filter changeover, cleaning)? |  |  | 0 | TBC181 | 181
Y2 | Is the design of the individual treatment system appropriate for the nature of the raw water quality? |  |  | 0 | TBC182 | 182
Z1 | CONFIDENCE IN MANAGEMENT? To determine the risk rating for this section, answer questions Z2 to Z27 to inform the answer to Z1.There should only one risk rating for this section in Z1. |  |  | 0 | TBC183 | 183
Z2 | Are records kept of key checks e.g. Equipment maintenance, site inspections, on-site tests, etc |  |  | 0 | TBC184 | 184
Z3 | Are there written procedures for the operation and maintenance of equipment? |  |  | 0 | TBC185 | 185
Z4 | Are there procedures for responding to alarms, monitors, on-site tests? |  |  | 0 | TBC186 | 186
Z5 | Is there a written procedure for installations, pipe repairs and maintenance to protect against microbial contamination? |  |  | 0 | TBC187 | 187
Z6 | Do operators have adequate (even if informal) general hygiene awareness? |  |  | 0 | TBC188 | 188
Z7 | Is there a documented procedure for operation of valves including authorisation? |  |  | 0 | TBC189 | 189
Z8 | Are there any records of reservoir cleaning and maintenance? |  |  | 0 | TBC190 | 190
Z9 | Are the records checked to ensure the required maintenance and checks have been carried out satisfactorily? |  |  | 0 | TBC191 | 191
Z10 | Is there a stock control process for any chemicals used to ensure their continuous availability? |  |  | 0 | TBC192 | 192
Z11 | Is there a stock control process for any key spare parts/equipment? |  |  | 0 | TBC193 | 193
Z12 | Is there a documented contingency plan in the event of power failure, equipment failure? |  |  | 0 | TBC194 | 194
Z13 | Is the person nominated to manage the supply trained to run and maintain the supply? |  |  | 0 | TBC195 | 195
Z14 | Is there a nominated person to run the supply when the above person is unavailable? |  |  | 0 | TBC196 | 196
Z15 | Is there a documented system to report emergencies to management/owner of supply? |  |  | 0 | TBC197 | 197
Z16 | Are there calibration schedules in place for key dosing and monitoring equipment? |  |  | 0 | TBC198 | 198
Z17 | Is there a weekly site inspection to check for changes (e.g. Dead sheep, broken fence)? |  |  | 0 | TBC199 | 199
Z18 | Are there appropriate procedures for rectifying customer complaints? |  |  | 0 | TBC200 | 200
Z19 | Are there procedures and records in place to inform the LA of any changes to the risk assessment? |  |  | 0 | TBC201 | 201
Z20 | If a risk assessment has previously been carried out, is there a plan for delivering the required improvements? |  |  | 0 | TBC202 | 202
Z21 | Is there a detailed plan of the site including details of source, tanks, distribution pipes, valves (material, age) etc. |  |  | 0 | TBC203 | 203
Z22 | Is there a documented contingency for the supply running out? |  |  | 0 | TBC204 | 204
Z23 | Do the treatment chemicals and materials conform to Regulation 5? Have all new installations since 2010 complied with Regulation 5 (or equivalent in Wales) – products and processes |  |  | 0 | TBC205 | 205
Z24 | Do all materials involved in the distribution system conform to Regulation 5? Have all new installations since 2010 complied with Regulation 5 (or equivalent in Wales) – products and processes? |  |  | 0 | TBC206 | 206
Z25 | Is there a documented procedure for carrying out mains tappings (making new connections into pipes)? |  |  | 0 | TBC207 | 207
Z26 | Are persons carrying out this work competent and trained in this procedure?(e.g. approved by a water company or part of the Water Safe Scheme)? |  |  | 0 | TBC208 | 208

## Risk_Register
Private Water Supply: Risk Assessment Register Guidance: Select your risk level
Risk level: | TBC | Local Authority: Supply Reference: |  |  |  |  | VH | Very High Risk
To Be confirmed |  | Supply Name & Address: |  |  |  |  | H | High Risk
Risk | Risk No. | Hazard Description | Likelihood | Severity |  |  | M | Medium Risk
TBC | A0 | Have there been any changes since risk assessment last carried out? | 5 | 0 | TBC1 | 1 | L | Low Risk
TBC | A1 | Is there a site plan and/or schematic showing location of source, chambers, tanks, distribution network including valves, pipes, consumer premises etc.? | 5 | 5 | TBC2 | 2 | TBC | To Be confirmed
TBC | A2 | Are there any procedures and/or written records for the supply (i.e. for checks, monitoring or maintenance, etc.)? | 5 | 5 | TBC3 | 3
TBC | A3 | Are there any manufacturers' instructions for the equipment on the supply? | 5 | 5 | TBC4 | 4
TBC | A4 | Is there an emergency plan for the provision of an alternative water supply? | 5 | 5 | TBC5 | 5
TBC | A5 | Has the owner or operators had appropriate training for the supply? | 5 | 5 | TBC6 | 6
TBC | A6 | Does the sampling history identify the presence of any hazards? | 5 | 3 | TBC7 | 7
TBC | B1 | Are there latrines, septic tanks, animal enclosures or cess pits present within 50m of the source? | 0 | 4 | TBC8 | 8
TBC | B2 | Are there any waste pipes (sewage) adjacent to the source? | 0 | 4 | TBC9 | 9
TBC | B3 | Is there a risk of microbial contamination (from slurry spreading, and/or storage of slurry or dung)? | 0 | 5 | TBC10 | 10
TBC | B4 | Is there a risk of pesticides or chemical contamination (e.g. sheep dipping chemicals) | 0 | 4 | TBC11 | 11
TBC | B5 | Are chemical fertilisers used? | 0 | 4 | TBC12 | 12
TBC | B6 | Is there history of mining in the catchment (i.e. chemical or metal contamination)? | 0 | 4 | TBC13 | 13
TBC | B7 | Does the local geology suggest the present of - boron, arsenic, lead, fluoride, uranium, nickel, radon or other potentially harmful natural substance in raw water? | 0 | 4 | TBC14 | 14
TBC | B8 | Is the source likely to be affected by any contaminated land including landfill sites in the catchment? | 0 | 4 | TBC15 | 15
TBC | B9 | Is there a likelihood of insufficiency of supply i.e. over-abstraction of source or during drought conditions | 0 | 4 | TBC16 | 16
TBC | B10 | Is the source adequately protected against vandalism (deliberate contamination of source and unauthorised access)? | 0 | 5 | TBC17 | 17
TBC | B11 | Is there a risk of oil spill entering the supply (e.g. generators, household heating oil, farm fuel, generators, road traffic accident or the presence of a redundant tanker etc.)? | 0 | 5 | TBC18 | 18
TBC | B15 | Are there any man made sources of tritium in the catchment which could affect the water supply? | 0 | 5 | TBC19 | 19
TBC | B16 | Has the Environment Agency any record of historic pollution event(s) in the catchment which contained radioactive substances? | 0 | 5 | TBC20 | 20
TBC | B17 | Does the local water company have a notice allowing them to cease monitoring for tritium or ID for abstraction points from the same aquifer? | 0 | 5 | TBC21 | 21
TBC | B18 | Is there any monitoring data (EA/Wco/LA) for radioactive substances in this supply or another supply in the same water body indicating levels above the standard/value? | 0 | 5 | TBC22 | 22
TBC | B19 | Does the ‘Radioactivity in Food and the environment’ report indicate the likely presence of radioactive substances? | 0 | 4 | TBC23 | 23
TBC | B20 | If gross alpha or gross beta exceed the limit, does the Indicative Dose (ID)calculation confirm the value is <0.1mSv? | 0 | 5 | TBC24 | 24
TBC | C1 | Is there a noticeable change in the appearance of the water from time to time (colour, cloudiness/turbidity)? | 0 | 4 | TBC25 | 25
TBC | C2 | Is the source exposed to risks of faecal contamination from wildlife (this will always be yes for all surface water sources, i.e. rivers, lakes and streams)? | 0 | 3 | TBC26 | 26
TBC | C3 | Is there waste-water discharging biological matter into the source? | 0 | 5 | TBC27 | 27
TBC | C4 | Is there waste-water discharging chemical substances into the source? | 0 | 4 | TBC28 | 28
TBC | C5 | Are there unbunded stores of farm waste or silage in the catchment? | 0 | 5 | TBC29 | 29
TBC | C6 | Is local forestry activity causing or likely to cause suspended particles in the source water? | 0 | 3 | TBC30 | 30
TBC | C7 | Is freshwater aquaculture practised upstream, causing contamination (feed, pesticides etc.)? | 0 | 4 | TBC31 | 31
TBC | C8 | Is there run off from construction/development activities upstream of intake causing contamination (oil spills, silt, cement, bentonites, soakaways, open tanks, surface water inceptors)? | 0 | 4 | TBC32 | 32
TBC | C9 | Is local quarrying activity causing or likely to cause suspended particles or any chemicals in the source water? | 0 | 4 | TBC33 | 33
TBC | C10 | Is the source water used for recreational purposes? | 0 | 4 | TBC34 | 34
TBC | C11 | Is the source water subject to seasonal algal blooms including toxin producing algae (cyanobacteria)? | 0 | 3 | TBC35 | 35
TBC | C12 | Is the spring chamber designed and constructed to exclude surface water or spillages of contaminated material causing microbial or other contamination (through the cover or the lining) and is it in a satisfactory state of repair? | 0 | 5 | TBC36 | 36
TBC | C13 | Does the spring chamber extend at least 150mm above the level of the floor with an apron sloping away from a secure cover? | 0 | 5 | TBC37 | 37
TBC | D1 | Where there are abandoned wells or observation boreholes are they adequately capped, fenced and protected? | 0 | 4 | TBC38 | 38
TBC | D2 | Are livestock excluded from the vicinity of the headworks (e.g. by fencing) to minimise the risk of microbial contamination? | 0 | 5 | TBC39 | 39
TBC | D3 | Is there evidence of standing water/ponding within 50m of the headworks? | 0 | 4 | TBC40 | 40
TBC | D4 | Is the borehole or well appropriately lined with casing and grouted to prevent ingress of shallow subsurface and/or surface water? | 0 | 4 | TBC41 | 41
TBC | D5 | If a chamber is present does it have barrier(s) to prevent ingress of surface water through the walls/floor (grouting/diversion ditch/walls etc.)? | 0 | 5 | TBC42 | 42
TBC | D6 | If a chamber is present does it have a cover that is non-degradable material that would prevent ingress of rainwater, vermin and is lockable (if not inside a locked building)? | 0 | 5 | TBC43 | 43
TBC | D7 | Are the headworks completely sealed so that no surface water, spillages or vermin/insects can enter? | 0 | 4 | TBC44 | 44
TBC | D8 | Are there land drains which channel water into the source? | 0 | 5 | TBC45 | 45
TBC | D9 | Are there historic results from the supply confirming the radon levels are below 100Bq/l? | 0 | 5 | TBC46 | 46
TBC | D10 | Does the local water company have a waiver for radon for abstraction points in the same aquifer? | 0 | 5 | TBC47 | 47
TBC | D11 | Do radon-in-air measurements confirm the levels are below 200Bq/m3 (where there is no existing radon treatment)? | 0 | 4 | TBC48 | 48
TBC | D12 | Does the PHE report or AEA Ricardo report identify the site as moderate or high hazards rating? | 0 | 4 | TBC49 | 49
TBC | D13 | Do sample results indicate radon levels are greater than 1000Bq/l? | 0 | 5 | TBC50 | 50
TBC | D14 | Is the source exposed to risks of faecal contamination from wildlife | 0 | 5 | TBC51 | 51
TBC | E1 | Is there evidence the supply main is coal tar lined? | 0 | 4 | TBC52 | 52
TBC | E2 | Are there sediments in the main? | 0 | 3 | TBC53 | 53
TBC | E3 | Is the section of main upstream of the point of supply subject to good turnover of water (e.g. are there connections to properties nearby which would ensure the water is refreshed in the main constantly)? | 0 | 3 | TBC54 | 54
TBC | E4 | If the area feeding the supply has had water quality related complaints in the last 12 months, have the causes been mitigated? | 0 | 3 | TBC55 | 55
TBC | E5 | Have any chemical parameters exceeded the standard in the previous 12 months in the mains supply? | 0 | 5 | TBC56 | 56
TBC | E6 | Are there backflow protection deficiencies at any upstream industrial or commercial premises? | 0 | 4 | TBC57 | 57
TBC | I1 | Is there any protection against faecal or chemical contamination e.g. from wildlife or industrial emissions? | 0 | 5 | TBC58 | 58
TBC | I2 | Are there any screens to prevent material entering the collection chamber (e.g. leaves, insects, twigs)? | 0 | 4 | TBC59 | 59
TBC | I3 | Are there any trees overhanging the roof? | 0 | 4 | TBC60 | 60
TBC | I4 | Is there evidence of lead, tin, copper, asphalt, new galvanised sheeting or wood preservatives on the roof? | 0 | 4 | TBC61 | 61
TBC | I5 | Is there a bypass mechanism to exclude the first flush of rainwater from the roof? | 0 | 5 | TBC62 | 62
TBC | I6 | Is there adequate backflow protection for any rainwater harvesting systems in place at any of the properties? | 0 | 5 | TBC63 | 63
TBC | J1 | Does the water quality vary at the intake point due to streaming/stratification/algal blooms/increased turbidity? | 0 | 3 | TBC64 | 64
TBC | J2 | Are there screens in place at the intake? | 0 | 3 | TBC65 | 65
TBC | J3 | Where screens are present, is there a mechanism to remove debris? | 0 | 3 | TBC66 | 66
TBC | J4 | Does sediment build up inside the chamber and pipework after the intake point? | 0 | 3 | TBC67 | 67
TBC | J5 | Is there adequate protection of the intake point from livestock and wildlife? | 0 | 5 | TBC68 | 68
TBC | J6 | Does the availability of the water at the intake vary? | 0 | 3 | TBC69 | 69
TBC | K1 | Is there a regular turn over of water? | 0 | 3 | TBC70 | 70
TBC | K2 | Are the storage tanks vulnerable to ingress, flooding or other microbial contamination (e.g. wildlife access)? | 0 | 4 | TBC71 | 71
TBC | K3 | Is there a stock-proof fence around any inspection chambers? | 0 | 4 | TBC72 | 72
TBC | K4 | Are the tanks regularly maintained to preserve their structural integrity and cleaned? | 0 | 4 | TBC73 | 73
TBC | K5 | Are the storage tanks adequately protected against vandalism? | 0 | 4 | TBC74 | 74
TBC | K6 | Is the cleaning regime for the tank appropriate? | 0 | 4 | TBC75 | 75
TBC | L1 | Is there adequate Cryptosporidium treatment in place? | 0 | 5 | TBC76 | 76
TBC | L2 | Is the treatment plant operating within the design capacity? | 0 | 5 | TBC77 | 77
TBC | L3 | Is it possible to by-pass any stage of treatment? | 0 | 5 | TBC78 | 78
TBC | L4 | Where there is a blending facility, is there an appropriate blending strategy? | 0 | 4 | TBC79 | 79
TBC | L5 | Are there frequent flow variations through the treatment plant, which render the treatment process inadequate? | 0 | 4 | TBC80 | 80
TBC | L6 | Are there frequent demand variations, which could cause insufficiency? | 0 | 3 | TBC81 | 81
TBC | M1 | Is there adequate pre-treatment (e.g. clarification) in place if required? | 0 | 5 | TBC82 | 82
TBC | M2 | Is there adequate process control for filtration (e.g. turbidity monitors)? | 0 | 5 | TBC83 | 83
TBC | M3 | Can the filters overload? | 0 | 5 | TBC84 | 84
TBC | M4 | Do the filters block? | 0 | 5 | TBC85 | 85
TBC | M5 | Is the media depth at a minimum to design specification? | 0 | 5 | TBC86 | 86
TBC | M6 | Is the filter media composition as per design specification? | 0 | 5 | TBC87 | 87
TBC | M7 | Is the backwashing regime operated to the design manual (including cycle length, uneven scour, pump failure, loss of filter media) | 0 | 5 | TBC88 | 88
TBC | M8 | Do the filters appear well maintained? | 0 | 5 | TBC89 | 89
TBC | M9 | Does the water run to waste when rapid gravity filters are started up? | 0 | 5 | TBC90 | 90
TBC | M10 | Can the filters be started up gradually (i.e. not immediately run at full capacity)? | 0 | 5 | TBC91 | 91
TBC | M11 | Where Cryptosporidium is potentially present in the raw water, is a turbidity of less than 1.0 NTU achieved in the filtered water? | 0 | 5 | TBC92 | 92
TBC | M12 | Is the backwash water recycled to head of works? | 0 | 5 | TBC93 | 93
TBC | M13 | Is algal growth apparent in/on filters? | 0 | 3 | TBC94 | 94
TBC | M14 | For slow sand filters, is the required ripening period adhered to before putting the water into supply? | 0 | 5 | TBC95 | 95
TBC | N1 | Has the GAC been installed as per the design specification? | 0 | 5 | TBC96 | 96
TBC | N2 | Is the GAC design appropriate for the nature of the raw water quality? | 0 | 5 | TBC97 | 97
TBC | N3 | Is the media depth and composition appropriate for the nature of the raw water quality? | 0 | 4 | TBC98 | 98
TBC | N4 | Is the plant regularly operated and maintained according to the design specification? | 0 | 4 | TBC99 | 99
TBC | O1 | Is the treatment plant operating within its design capacity? | 0 | 5 | TBC100 | 100
TBC | O2 | Is there adequate pre-treatment (e.g. filtration) in place if required? | 0 | 5 | TBC101 | 101
TBC | O3 | Is the media depth at a minimum to design specification? | 0 | 5 | TBC102 | 102
TBC | O4 | Is the ion exchange media composition as per design specification? | 0 | 5 | TBC103 | 103
TBC | O5 | Is there a suitable maintenance schedule? | 0 | 4 | TBC104 | 104
TBC | O6 | Is the regeneration regime as per design specification? | 0 | 5 | TBC105 | 105
TBC | P1 | Does the plant design take into account the raw water quality? | 0 | 5 | TBC106 | 106
TBC | P2 | Is there adequate pre-treatment to prevent membrane fouling and damage? | 0 | 5 | TBC107 | 107
TBC | P3 | Are the cleaning regimes (for descaling and antifouling, etc.) being followed as set out in the design specification? | 0 | 5 | TBC108 | 108
TBC | P4 | Are the chemicals used in the process as recommended by the manufacturer? | 0 | 5 | TBC109 | 109
TBC | P5 | Is there a procedure to confirm that the integrity of the membrane is maintained? | 0 | 5 | TBC110 | 110
TBC | P6 | Are the filters replaced as per the manufacturer's specifications (or more frequently)? | 0 | 5 | TBC111 | 111
TBC | P7 | Was the raw water quality taken into account when the filters were installed? | 0 | 5 | TBC112 | 112
TBC | Q1 | Is there any likelihood of industrial, domestic or boating waste flows in the vicinity of the water intake to the desalination plant? | 0 | 5 | TBC113 | 113
TBC | Q2 | Could any chemical stores potentially contaminate the supply at the intake? | 0 | 4 | TBC114 | 114
TBC | Q3 | Are there variations in source water levels, which affect the ability to abstract water? | 0 | 3 | TBC115 | 115
TBC | Q4 | Is there adequate treatment to prevent membrane fouling and damage? | 0 | 4 | TBC116 | 116
TBC | Q5 | Are oxidants removed during pretreatment? | 0 | 3 | TBC117 | 117
TBC | Q6 | Has the operator mitigated against the demineralisation of the water? | 0 | 3 | TBC118 | 118
TBC | Q7 | Is the treated supply blended with other sources of drinking water in distribution? | 0 | 4 | TBC119 | 119
TBC | Q8 | Are the chemicals used in the process as recommended by the manufacturer? | 0 | 4 | TBC120 | 120
TBC | Q9 | Is the plant design appropriate for the nature of the raw water quality? | 0 | 5 | TBC121 | 121
TBC | R1 | Is there adequate preliminary treatment in place? | 0 | 5 | TBC122 | 122
TBC | R2 | Is there a validation certificate for the UV system? | 0 | 4 | TBC123 | 123
TBC | R3 | Can water be supplied if the U.V. is not operational? | 0 | 5 | TBC124 | 124
TBC | R4 | Is the UV operating within its validated range for the product type or lamp? | 0 | 5 | TBC125 | 125
TBC | R5 | Is the equipment regularly maintained e.g. bulb replacement, cleaning? | 0 | 5 | TBC126 | 126
TBC | S1 | Is there a backup/standby system for automatic chlorine dosing or an automatic shutdown arrangement? | 0 | 5 | TBC127 | 127
TBC | S2 | Is there evidence that maintenance has been carried out of the disinfection system within the last 12 months? | 0 | 5 | TBC128 | 128
TBC | S3 | Is there an appropriate alarm in the event of loss of chlorine dosing? | 0 | 5 | TBC129 | 129
TBC | S4 | Are the chemicals of drinking water grade i.e. approved for use in drinking water supplies? | 0 | 3 | TBC130 | 130
TBC | S5 | Is the existing dosing effective? | 0 | 5 | TBC131 | 131
TBC | T1 | Are all chemicals used for water treatment approved and in date? | 0 | 5 | TBC132 | 132
TBC | T2 | Are there controls in place for chemical deliveries to avoid chemicals being added to the wrong storage vessel? | 0 | 4 | TBC133 | 133
TBC | T3 | Are chemical injection point(s) protected against potential damage e.g. covered, frost proofing, etc? | 0 | 5 | TBC134 | 134
TBC | T4 | Are there procedures in place to ensure treatment is re-established after any loss of power supply? | 0 | 5 | TBC135 | 135
TBC | T5 | Is there a power back-up or alternative power supply? | 0 | 5 | TBC136 | 136
TBC | T6 | Is the treatment plant adequately protected against vandalism? | 0 | 5 | TBC137 | 137
TBC | T7 | Is the site liable to flooding which would result in loss or restriction of treatment process? | 0 | 5 | TBC138 | 138
TBC | T8 | Could access to the plant be lost or restricted due to weather extremes or other events? | 0 | 4 | TBC139 | 139
TBC | T9 | Could adverse weather conditions render the treatment process and/or chemicals ineffective? | 0 | 5 | TBC140 | 140
TBC | T10 | Are stored chemicals or oil adequately bunded? | 0 | 4 | TBC141 | 141
TBC | U1 | Are there appropriate online monitors? | 0 | 5 | TBC142 | 142
TBC | U2 | Are they calibrated and maintained? | 0 | 5 | TBC143 | 143
TBC | U3 | Do the on-line monitors have alarms? | 0 | 3 | TBC144 | 144
TBC | U4 | If monitors are not present on the supply, is any on-site testing being carried out? | 0 | 3 | TBC145 | 145
TBC | U5 | Is there a basic schematic for the treatment and monitoring equipment? | 0 | 3 | TBC146 | 146
TBC | V1 | After treatment is the water fully compliant with quality standards? | 0 | 5 | TBC147 | 147
TBC | V2 | Are there latrines, septic tanks, waste pipes, animal enclosures or cess pits present in the vicinity of the distribution system? | 0 | 5 | TBC148 | 148
TBC | V3 | Is there evidence of disinfection by-products in the network (e.g. taste problems due to THM's)? | 0 | 4 | TBC149 | 149
TBC | V4 | If chlorine disinfection is practiced is there a disinfectant residual in the distribution network? | 0 | 3 | TBC150 | 150
TBC | V5 | Is there a suitable written procedure for mains repair and maintenance? | 0 | 5 | TBC151 | 151
TBC | V6 | Is there history of any fractures or faults in the distribution system which could allow ingress of contamination? | 0 | 4 | TBC152 | 152
TBC | V7 | Is there any other route by which contamination can enter the distribution network via back-flow? If there is ponding of surface water or poor drainage, could water be pulled into the system during low pressure or changes in pressure, e.g. backflow from hoses, taps, or standpipes? | 0 | 4 | TBC153 | 153
TBC | V8 | Is there evidence any pipes are coal tar lined? | 0 | 4 | TBC154 | 154
TBC | V9 | Do any third parties have access to hydrants or other points in the distribution system? | 0 | 5 | TBC155 | 155
TBC | V10 | Is there potential contamination of plastic pipes through designated contaminated land, oil from generators/household fuel tanks/fuel stores or solvent spillage? | 0 | 4 | TBC156 | 156
TBC | V11 | Are there any pipes exposed and at risk of damage by any means e.g. vermin, vehicle, UV/sunlight damage, overheating or freezing? | 0 | 4 | TBC157 | 157
TBC | V12 | If there are valves in the network which are normally closed, are there measures in place to control when and how they are operated? | 0 | 2 | TBC158 | 158
TBC | V13 | Are there sections of pipework containing stagnant water? | 0 | 2 | TBC159 | 159
TBC | V14 | Where there is copper pipework present, is it corroding? | 0 | 3 | TBC160 | 160
TBC | V15 | Is there the potential for backflow from commercial premises, domestic premises, unauthorised connections, standpipes or unregulated supplies? | 0 | 5 | TBC161 | 161
TBC | V16 | Are lead pipes present in the supply? | 0 | 4 | TBC162 | 162
TBC | V17 | Do all junctions in the supply network, particularly animal watering systems and standpipes, have backflow protection? | 0 | 5 | TBC163 | 163
TBC | V18 | Are there any known or potential cross-connections (between different sources, greywater systems, sewage pipes or other waste pipes)? | 0 | 5 | TBC164 | 164
TBC | V19 | Have there been complaints or reports of water quality problems (e.g. taste, odours or reports of any aquatic animals (freshwater shrimp, louse or worms)? | 0 | 3 | TBC165 | 165
TBC | W1 | Are all treated water reservoirs covered appropriately e.g. No risk of ingress and/or constructed of suitable material? | 0 | 4 | TBC166 | 166
TBC | W2 | Are all treated water reservoirs of sufficient structural integrity to prevent ingress of contamination, including covers? | 0 | 4 | TBC167 | 167
TBC | W3 | Is the integrity of the reservoir suitably robust against damage by weather or animals? | 0 | 4 | TBC168 | 168
TBC | W4 | Are there any waste water pipes, or waste water storage tanks adjacent to the tanks/reservoirs? | 0 | 4 | TBC169 | 169
TBC | W5 | Are there any unprotected or inadequately protected access covers and/or vents? | 0 | 4 | TBC170 | 170
TBC | W6 | Are any treated water reservoirs adequately protected against solar heat gain, vandalism (deliberate contamination of treated water and unauthorised access)? | 0 | 4 | TBC171 | 171
TBC | W7 | Is there a stock-proof fence around any inspection chambers? | 0 | 4 | TBC172 | 172
TBC | W8 | Are the reservoirs regularly maintained and cleaned with appropriate records? | 0 | 4 | TBC173 | 173
TBC | W9 | Is there a regular turn over of water, such that the capacity of the storage vessel matches demand? | 0 | 3 | TBC174 | 174
TBC | X1 | Is the drinking water supply to any customer premises (kitchen tap) supplied via a loft tank? Note; there is no need to inspect loft tanks, just ask for evidence. If no, move on to question X4. | 0 | 5 | TBC175 | 175
TBC | X2 | If yes, do all loft tanks have a robust vermin proof cover? | 0 | 4 | TBC176 | 176
TBC | X3 | If yes, is there evidence the loft tanks are cleaned at least once per year? | 0 | 3 | TBC177 | 177
TBC | X4 | Is there any lead pipe work within the properties? | 0 | 4 | TBC178 | 178
TBC | X5 | Is the water at the consumers tap clear, taste and odour-free? | 0 | 2 | TBC179 | 179
TBC | X6 | Is there adequate backflow protection for any rainwater harvesting systems in place at any of the properties? | 0 | 5 | TBC180 | 180
TBC | Y1 | Is the treatment system maintained to the manufacturer's instructions (filter changeover, cleaning)? | 0 | 5 | TBC181 | 181
TBC | Y2 | Is the design of the individual treatment system appropriate for the nature of the raw water quality? | 0 | 5 | TBC182 | 182
TBC | Z1 | CONFIDENCE IN MANAGEMENT? To determine the risk rating for this section, answer questions Z2 to Z27 to inform the answer to Z1.There should only one risk rating for this section in Z1. | 0 | 5 | TBC183 | 183
TBC | Z2 | Are records kept of key checks e.g. Equipment maintenance, site inspections, on-site tests, etc | 0 | 0 | TBC184 | 184
TBC | Z3 | Are there written procedures for the operation and maintenance of equipment? | 0 | 0 | TBC185 | 185
TBC | Z4 | Are there procedures for responding to alarms, monitors, on-site tests? | 0 | 0 | TBC186 | 186
TBC | Z5 | Is there a written procedure for installations, pipe repairs and maintenance to protect against microbial contamination? | 0 | 0 | TBC187 | 187
TBC | Z6 | Do operators have adequate (even if informal) general hygiene awareness? | 0 | 0 | TBC188 | 188
TBC | Z7 | Is there a documented procedure for operation of valves including authorisation? | 0 | 0 | TBC189 | 189
TBC | Z8 | Are there any records of reservoir cleaning and maintenance? | 0 | 0 | TBC190 | 190
TBC | Z9 | Are the records checked to ensure the required maintenance and checks have been carried out satisfactorily? | 0 | 0 | TBC191 | 191
TBC | Z10 | Is there a stock control process for any chemicals used to ensure their continuous availability? | 0 | 0 | TBC192 | 192
TBC | Z11 | Is there a stock control process for any key spare parts/equipment? | 0 | 0 | TBC193 | 193
TBC | Z12 | Is there a documented contingency plan in the event of power failure, equipment failure? | 0 | 0 | TBC194 | 194
TBC | Z13 | Is the person nominated to manage the supply trained to run and maintain the supply? | 0 | 0 | TBC195 | 195
TBC | Z14 | Is there a nominated person to run the supply when the above person is unavailable? | 0 | 0 | TBC196 | 196
TBC | Z15 | Is there a documented system to report emergencies to management/owner of supply? | 0 | 0 | TBC197 | 197
TBC | Z16 | Are there calibration schedules in place for key dosing and monitoring equipment? | 0 | 0 | TBC198 | 198
TBC | Z17 | Is there a weekly site inspection to check for changes (e.g. Dead sheep, broken fence)? | 0 | 0 | TBC199 | 199
TBC | Z18 | Are there appropriate procedures for rectifying customer complaints? | 0 | 0 | TBC200 | 200
TBC | Z19 | Are there procedures and records in place to inform the LA of any changes to the risk assessment? | 0 | 0 | TBC201 | 201
TBC | Z20 | If a risk assessment has previously been carried out, is there a plan for delivering the required improvements? | 0 | 0 | TBC202 | 202
TBC | Z21 | Is there a detailed plan of the site including details of source, tanks, distribution pipes, valves (material, age) etc. | 0 | 0 | TBC203 | 203
TBC | Z22 | Is there a documented contingency for the supply running out? | 0 | 0 | TBC204 | 204
TBC | Z23 | Do the treatment chemicals and materials conform to Regulation 5? Have all new installations since 2010 complied with Regulation 5 (or equivalent in Wales) – products and processes | 0 | 0 | TBC205 | 205
TBC | Z24 | Do all materials involved in the distribution system conform to Regulation 5? Have all new installations since 2010 complied with Regulation 5 (or equivalent in Wales) – products and processes? | 0 | 0 | TBC206 | 206
TBC | Z25 | Is there a documented procedure for carrying out mains tappings (making new connections into pipes)? | 0 | 0 | TBC207 | 207
TBC | Z26 | Are persons carrying out this work competent and trained in this procedure?(e.g. approved by a water company or part of the Water Safe Scheme)? | 0 | 0 | TBC208 | 208

## Risk_Assessment_Report
Private Water Supply: Risk Assessment Report
Local Authority: |  |  | Supply Reference:
Supply Name & Address: |  |  | 0
Risk number and description |  |  | Due date | Action Owner | Risk mitigation actions required
Main Risk | #N/A | #N/A | 0 | Enter name or initials | Description of the actions required to mitigate the risks
Main Risk | #N/A | #N/A | 0 | Enter name or initials | Description of the actions required to mitigate the risks
Main Risk | #N/A | #N/A | 0 | Enter name or initials | Description of the actions required to mitigate the risks
Main Risk | #N/A | #N/A | 0 | Enter name or initials | Description of the actions required to mitigate the risks
Main Risk | #N/A | #N/A | 0 | Enter name or initials | Description of the actions required to mitigate the risks
Main Risk | #N/A | #N/A | 0 | Enter name or initials | Description of the actions required to mitigate the risks
Main Risk | #N/A | #N/A | 0 | Enter name or initials | Description of the actions required to mitigate the risks
Main Risk | #N/A | #N/A | 0 | Enter name or initials | Description of the actions required to mitigate the risks
Main Risk | #N/A | #N/A | 0 | Enter name or initials | Description of the actions required to mitigate the risks
Main Risk | #N/A | #N/A | 0 | Enter name or initials | Description of the actions required to mitigate the risks
Ref | Hazard | Answer | Risk | Guidance
A0 | Have there been any changes since risk assessment last carried out? | TBC - No risk | TBC | Any changes to the equipment, ownership or management should result is a 'Yes' Please use the severity option to determine if these changes are an improvement or deterioration
A1 | Is there a site plan and/or schematic showing location of source, chambers, tanks, distribution network including valves, pipes, consumer premises etc.? | TBC - No risk | TBC | A site plan or schematic can be a simple sketch through to a complex engineering drawing depending on the size of the supply. It need not be to scale or include internal domestic plumbing arrangements, but should represent the main components of the supply system. It is essential to understand the layout of the water supply system in order to understand the flow of water from source to tap, and how it is managed and monitored, e.g.by valves, meters and other management devices. If no schematic or site plan is present, risk assessment of the site is difficult if not impossible to achieve. If not present the likelihood should be scored as 5, the person in control should be requested to make arrangements to draw up plans showing any valves, meters, hydrants etc as part of the action plan
A2 | Are there any procedures and/or written records for the supply (i.e. for checks, monitoring or maintenance, etc.)? | TBC - No risk | TBC | An absence of written procedures places reliance on specific individuals, who may not always be available to operate the supply system. Procedures provide a reference for operators and ensure a consistent approach. Records of maintenance and monitoring checks provide a management audit trail, which demonstrate how well a supply is being managed and its performing. If these are absent the person in control should be required to implement them.
A3 | Are there any manufacturers' instructions for the equipment on the supply? | TBC - No risk | TBC | The presence of manufacturers' instructions for key equipment (e.g. pumps, treatment processes, dosing systems, monitors) provides an essential reference for operators and provides a record of equipment requirements as designed. Where any instructions are absent, they should be sought as part of the action plan.
A4 | Is there an emergency plan for the provision of an alternative water supply? | TBC - No risk | TBC | Loss of supplies can occur for a variety of reasons, which are often unforeseen. Contingency measures to provide alternative supplies should be documented as written procedures to ensure that the relevant people can reference what to do under these circumstances.DWI have provided guidance on the provision of alternative supplies, which can be obtained from their website. Persons in control should demonstrate that procedures are in place.
A5 | Has the owner or operators had appropriate training for the supply? | TBC - No risk | TBC | Operators should be competent in the operation of the supply system they are managing, and have an understanding of the need to apply sound hygienic practice. A lack of competency and/or hygiene awareness presents a risk of contamination of the supply. The risk assessor must determine what and when training has been undertaken, and whether it is appropriate. For a complex treatment system such as chlorination or chlorine dioxide disinfection a formal training course maybe required, whereas for a UV system informal training form the supplier with written procedures could be appropriate. This can be achieved through dialogue and evidence through certification or other written records. A judgement as to whether deficiencies present a risk must be made and relevant advice provided.
A6 | Does the sampling history identify the presence of any hazards? | TBC - No risk | TBC | Is the supply sampled, excluding regulatory LA sampling, (i.e. operational)? Confirm what parameters the sample is analysed for and what are the results? Determine if this sampling has identified the presence of any particular hazards which should inform the risk assessment.
Section B - SOURCE: All catchments
B1 | Are there latrines, septic tanks, animal enclosures or cess pits present within 50m of the source? | TBC - No risk | TBC | If unsewered human or animal sanitation is present within 50m of the source then there is considerable potential for raw human sewage to contaminate the source of the drinking water supply. If the supply is groundwater and in a high vulnerability area (as indicated in the EA aquifer vulnerability maps), the unsewered human or animal sanitation is highly likely to contaminate the source through underground connectivity. Information on geography and aquifers can be found in teh EA's Magic Maps available on the EA website or magic.defra.gov.uk In high vulnerability areas this contamination risk will be present regardless of the condition of the collection chamber or head works. New sources should not be installed within 50m of unsewered human or animal waste in high vulnerability areas.
B2 | Are there any waste pipes (sewage) adjacent to the source? | TBC - No risk | TBC | Defects, deterioration and damage to waste pipes may allow their contents to leach into the soil and enter the source where its integrity is compromised. Determine their contents, material, location (on a site plan) and where possible, their robustness (consider its age) to establish the likelihood of the hazard presented. Consider whether the pipe(s) could be relocated to lower depth ( avoiding damage) or moved to reduce the risk posed. All contractors on site should be made aware of the location of waste pipes when working in the area. To find information on groundwater vulnerability type the post code into the EA web page 'What's in your backyard' and look at the aquifer vulnerability map in the ground water section.
B3 | Is there a risk of microbial contamination (from slurry spreading, and/or storage of slurry or dung)? | TBC - No risk | TBC | The hazard arises from the active application of the materials in conjunction with the disruption of the soil itself, e.g. via ploughing or sub-soil injection. The likelihood value will be based on the probable duration and frequency at which such activities are undertaken. In some areas brownfield sites or derelict land will be remediated using sewage-derived sludge or slurry or similar materials. The rate of application will typically be higher and this should be borne in mind when assessing the risk. To find information on groundwater vulnerability type the post code into the EA web page 'What's in your backyard' and look at the aquifer vulnerability map in the ground water section.
B4 | Is there a risk of pesticides or chemical contamination (e.g. sheep dipping chemicals) | TBC - No risk | TBC | If storage / disposal sites for pesticides are known to be close to the source under investigation then the risk characterisation should reflect this. In addition, look for any evidence of sheep dipping activity in the area when assessing the site. Pesticides may also be periodically applied to the land - the timing of which and the nature of the pesticide will depend on the crops being grown or the livestock present.
B5 | Are chemical fertilisers used? | TBC - No risk | TBC | Chemical fertilizers typically contain nitrates and phosphates, which may enter watercourses through run-off or leaching. Levels will vary depending on the rates of application, weather conditions and the longer term history of applications at the site.
B6 | Is there history of mining in the catchment (i.e. chemical or metal contamination)? | TBC - No risk | TBC | If there is evidence of the area adjacent to the source having been used for mining activity at any time in the past, which may pose a contamination threat then this should be recorded on the risk assessment. Such activities may include mineral, ores or other extraction such as coal mining. The likely hazards include sediment/turbidity from the extraction itself or increased run-off times into water courses, or heavy metals depending on the material being mined.
B7 | Does the local geology suggest the present of - boron, arsenic, lead, fluoride, uranium, nickel, radon or other potentially harmful natural substance in raw water? | TBC - No risk | TBC | Minerals and substances such as these parameters are naturally occurring and are likely to be known by the water company, Environment Agency or other Local Authorities who have already carried out risk assessments. Because these are naturally occurring they are likely to affect large areas. the EA or neighbouring authorities are the best sources of ifnoramtion regarding the presence of such substances in the ground water. If the local water company has sources in the area they may be able to confirm or rule out the presence of such substances.
B8 | Is the source likely to be affected by any contaminated land including landfill sites in the catchment? | TBC - No risk | TBC | The presence of disposal sites may influence the quality of water at the source by allowing the introduction of microbiological or chemical contaminants into the supply, depending on the nature of the materials being disposed. Incineration is also included in this section as the question of both airborne material and disposal sites for ash residues need to be considered when making the overall assessment of the likely impact on the water quality at the source. the likelihood score should reflect the permanent nature (or longevity) of such sites in terms of their potential to continue to release polluting materials for many years after their immediate use has ceased. This question may include designated contaminated land sites or sites that are potentially contaminated, which have not been designated.
B9 | Is there a likelihood of insufficiency of supply i.e. over-abstraction of source or during drought conditions | TBC - No risk | TBC | Insufficiency caused by low levels of stored water may result in for example (not an exhaustive list) increased algal population (due to increased temperature and sunlight), limescale deposits in ground water, sludge, metal concentrations and reduced oxygen levels. The insufficiency of supplies is a hazard in itself, additionally there are hazards associated with the water levels recharging or replenishing such as increased turbidity, nitrates, pesticides, or cryptosporidium from run-off.
B10 | Is the source adequately protected against vandalism (deliberate contamination of source and unauthorised access)? | TBC - No risk | TBC | Adequate protection will be site specific depending on the level of accessibility of the site to the general public. Measures may include fencing, gates and padlocks, etc.
B11 | Is there a risk of oil spill entering the supply (e.g. generators, household heating oil, farm fuel, generators, road traffic accident or the presence of a redundant tanker etc.)? | TBC - No risk | TBC | Are there fuel stores (e.g. domestic tanks) or equipment using fuel, stored within 250m of the source? Check their condition (are they in good repair and adequately bunded and the suitability of their filling procedure to determine the likelihood.
B12 | 0 | N/A - No risk |  | No guidance available
B13 | 0 | N/A - No risk |  | No guidance available
B14 | 0 | N/A - No risk |  | No guidance available
Section B - Radioactivity
B15 | Are there any man made sources of tritium in the catchment which could affect the water supply? | TBC - No risk | TBC | Man-made sources of tritium are uncommon in England and Wales, and would be as a result of contamination events, discharges or spills. Consult local authority records and the Environment Agency (NRW in Wales) for information on known spills or disposal of tritium.
B16 | Has the Environment Agency any record of historic pollution event(s) in the catchment which contained radioactive substances? | TBC - No risk | TBC | Consult with the Environment Agency (NRW in Wales) for information on any historic pollution or contamination events. This should include its location, the nature of the contamination, what was the radioactive substance involved, details of any remediation carried out and details of any ongoing monitoring.
B17 | Does the local water company have a notice allowing them to cease monitoring for tritium or ID for abstraction points from the same aquifer? | TBC - No risk | TBC | Contact the supplying water company and request details of the evidence provided to justify this, results of any samples taken and confirm whether or not the company has been granted a waiver to allow them to reduce or cease analysis for radioactivity. These are valid for a 5yr period and should be used to help inform the risk assessment.
B18 | Is there any monitoring data (EA/Wco/LA) for radioactive substances in this supply or another supply in the same water body indicating levels above the standard/value? | TBC - No risk | TBC | If any organisation has monitoring results showing a radioactive substance above the permitted value, the supply should be classified as high or very high risk of exceeding the parametric value, pending further investigation and monitoring.
B19 | Does the ‘Radioactivity in Food and the environment’ report indicate the likely presence of radioactive substances? | TBC - No risk | TBC | https://www.food.gov.uk/science/research/radiologicalresearch/radiosurv/rife Where it is established that there is a likely presence of radioactive substances, further information relating to this should be obtained from the EA and PHE.
B20 | If gross alpha or gross beta exceed the limit, does the Indicative Dose (ID)calculation confirm the value is <0.1mSv? | TBC - No risk | TBC | If a result of gross alpha or gross beta is above the permitted values, further investigation should be carried out and analysis of individual radionuclides undertaken to calculate the ID. Your laboratory should be able to carry out this analysis and calculation. If it is below 0.1mSv no further monitoring of gross alpha or beta is required.
B21 | 0 | N/A - No risk |  | No guidance available
B22 | 0 | N/A - No risk |  | No guidance available
B23 | 0 | N/A - No risk |  | No guidance available
Section C - SOURCE: Catchment of Surface Water Supply (including springs)
C1 | Is there a noticeable change in the appearance of the water from time to time (colour, cloudiness/turbidity)? | TBC - No risk | TBC | Changes in levels and flows can result in deterioration of raw water quality with associated increases in turbidity and colour due to the suspension of sediment. This will be most prevalent during periods of heavy rainfall, when flooding and rapid runoff of surface water into the source can occur. Associated water treatment must be designed to meet the demands of these "flashy" conditions.
C2 | Is the source exposed to risks of faecal contamination from wildlife (this will always be yes for all surface water sources, i.e. rivers, lakes and streams)? | TBC - No risk | TBC | Any evidence of wildlife, mammals (rabbits, deer, etc.), birds (gulls, geese, migratory birds, etc) reptiles ( frogs, newts, etc) at the source could indicate the potential for contamination of the supply either from faecal material or from carcasses falling into the supply. Measures required to mitigate risks from wildlife should take into account the type and extent of risk presented. The occurrence of wildlife might be transient (e.g. from birds overhead) or more regular, where for example, the source is in close proximity to rabbit warrens.
C3 | Is there waste-water discharging biological matter into the source? | TBC - No risk | TBC | Determine (probably during desk top part of assessment) if any sewage treatment works, abattoirs, etc discharge waste upstream of the source intake.
C4 | Is there waste-water discharging chemical substances into the source? | TBC - No risk | TBC | Determine (probably during desk top part of assessment) if any tanneries, paint factories, plating works, etc discharge chemicals upstream of the source intake.
C5 | Are there unbunded stores of farm waste or silage in the catchment? | TBC - No risk | TBC | If there are areas where silage is being stored in polyethylene bags (or equivalent) or other farm-derived wastes (faecal contamination) where there is no bunded storage and there is the potential for spillage entering the source (including via land drains) which are permanent or long-term feature then the likelihood should be scored as 5 . The hazard is high ammonia levels which reduces the effectiveness of chlorine disinfection. Chlorination converts ammonia to chloramines which are less potent disinfectants than chlorine itself and can give rise to taste and odour complaints. Therefore, when designing chlorination systems for ammonia-containing waters, the chlorine capacity must be sufficient to produce a free chlorine residual.
C6 | Is local forestry activity causing or likely to cause suspended particles in the source water? | TBC - No risk | TBC | Forestry activities have the potential to increase suspended particles (soil/debris) in the water supplies of the area. The disruption may occur when forests are being planted, thinning activities or harvesting.
C7 | Is freshwater aquaculture practised upstream, causing contamination (feed, pesticides etc.)? | TBC - No risk | TBC | i.e. fish farms. Hazards associated with fish farms are pesticides, particulates from organics feed and waste material, including faecal.
C8 | Is there run off from construction/development activities upstream of intake causing contamination (oil spills, silt, cement, bentonites, soakaways, open tanks, surface water inceptors)? | TBC - No risk | TBC | If there is evidence of the area adjacent to the source having been used for industrial activity which may pose a contamination threat then this should be recorded on the risk assessment. Such activities may include chemical or pharmaceutical production, mineral or other extraction such as coal mining, areas where old fuel tanks may have been located or may still be in place either below or above ground, or industries where solvents would have been in use and may have been disposed of on to the ground, e.g. electroplating, metal working or electronics.
C9 | Is local quarrying activity causing or likely to cause suspended particles or any chemicals in the source water? | TBC - No risk | TBC | Local quarrying can increase suspended particles (dust/debris) in the water supplies of the area which can affect disinfection. Consider the level of activity to assess likelihood of hazard.
C10 | Is the source water used for recreational purposes? | TBC - No risk | TBC | Recreational water can become contaminated especially if there are boating activities, as boats can discharge oil, lavatory waste or other chemicals into the water. The risk of contamination of a PWS by oil or fuel can be reduced by installation of a boom surrounding the intake point.
C11 | Is the source water subject to seasonal algal blooms including toxin producing algae (cyanobacteria)? | TBC - No risk | TBC | The main hazard associated with algae is filter blocking however some species of blue green algae produce toxins. This is a seasonal occurrence therefore check with the person in control if they have experienced this at the supply. Assessment of the associated risk to public health is not straight forward. Such assessment should therefore take account of specialist advice such as "Blue -green algae (Cyanobacteria) in Inland Waters: Assessment and control of risks to public health.
C12 | Is the spring chamber designed and constructed to exclude surface water or spillages of contaminated material causing microbial or other contamination (through the cover or the lining) and is it in a satisfactory state of repair? | TBC - No risk | TBC | If the chamber is not in a satisfactory state of repair, the lining is not watertight (i.e. where there is deterioration of the cement lining, brick, stone or concrete rings by roots or by other damage) or does not have a watertight cover, then there is a risk of ingress into the spring chamber causing potentially contaminated surface water to enter the supply. If there is evidence that the chamber is not watertight then the likelihood score should reflect the almost certain nature of the hazard
C13 | Does the spring chamber extend at least 150mm above the level of the floor with an apron sloping away from a secure cover? | TBC - No risk | TBC | If the spring chamber does not extend above the level of the floor then there is an increased risk of the top of the spring chamber either being inundated with water, introducing contamination into the chamber . A secure lockable cover is required to prevent malicious (or just curious) persons gaining access to the supply. If there is no apron sloping away from the spring chamber cover, water can pond around the cover and ingress is likely. If there is evidence of this then the likelihood score is almost certain
C14 | 0 | N/A - No risk |  | No guidance available
C15 | 0 | N/A - No risk |  | No guidance available
C16 | 0 | N/A - No risk |  | No guidance available
Section D - SOURCE: Catchment of Ground Water Supply
D1 | Where there are abandoned wells or observation boreholes are they adequately capped, fenced and protected? | TBC - No risk | TBC | If there are unused supplies or wells associated with the supply under investigation then the potential for material to be introduced directly into the source water exists. For example, if an older, out of use well is located adjacent to the currently operational well, any contamination of the out of use well or borehole can affect the water source. To find information on groundwater vulnerability type the post code into the EA web page www.whatsinmybackyard and look at the aquifer vulnerability map in the ground water section. http://publications.environment-agency.gov.uk/PDF/SCHO1000BFHB-B-E.pdf
D2 | Are livestock excluded from the vicinity of the headworks (e.g. by fencing) to minimise the risk of microbial contamination? | TBC - No risk | TBC | Look for any evidence of domestic livestock production being present either directly (by the presence of animals in the vicinity of the supply) or indirectly (through presence of broken ground around the supply or the presence of animal droppings around the supply). http://publications.environment-agency.gov.uk/PDF/SCHO1000BFHB-B-E.pdf. Risks can be increased where the source is in a high vulnerability area ( see B1 Guidance).
D3 | Is there evidence of standing water/ponding within 50m of the headworks? | TBC - No risk | TBC | look for evidence of standing water around the source, or evidence standing water has been present (marshy ground). This indicates the soil around the source is more likely to be saturated and therefore any flow of surface water into the source will be faster. http://publications.environment-agency.gov.uk/PDF/SCHO1000BFHB-B-E.pdf. Risks can be increased where the source is in a high vulnerability area ( see B1 Guidance).
D4 | Is the borehole or well appropriately lined with casing and grouted to prevent ingress of shallow subsurface and/or surface water? | TBC - No risk | TBC | Surface water or subsurface flows can contaminate the borehole/well where there is inappropriate or absent grouting or lining material. This can be protected against through the use of appropriately engineered borehole arrangements. If suitable arrangements are absent from the site then the permanent nature of the deficiency results in a likelihood score of almost certain (value 5). http://publications.environment-agency.gov.uk/PDF/SCHO1000BFHB-B-E.pdf
D5 | If a chamber is present does it have barrier(s) to prevent ingress of surface water through the walls/floor (grouting/diversion ditch/walls etc.)? | TBC - No risk | TBC | The borehole needs to be protected from the ingress of surface flows (such as flooding). This can be accomplished in a variety of ways such as having a ditch surrounding the borehole (https://www.gov.uk/government/collections/groundwater-protection) with an impermeable lining and a suitable discharge downslope from the borehole conveying surface water away from the immediate vicinity of the borehole. It should be borne in mind that surface flows, while including flooding, are not restricted to flooding. In certain ground conditions the impermeable nature of the soil during periods of dry weather will produce a surface akin to concrete which will result in rainfall, e.g. a heavy summer downpour, running over the surface rather than percolating into the soil. Such conditions need to be protected against by use of appropriately engineered borehole arrangements.
D6 | If a chamber is present does it have a cover that is non-degradable material that would prevent ingress of rainwater, vermin and is lockable (if not inside a locked building)? | TBC - No risk | TBC | A properly constructed and well-fitting cover is essential to maintaining the integrity of the source. In addition boreholes require a properly constructed and maintained chamber around the headworks with an inspection cover. The borehole/well casing should extend at least 150mm above the level of the floor and there should be a concrete apron, sloping away from the top of the borehole to ensure that any ingress to the housing will always run away from the top of the borehole. Covers should be of a suitable non degradable material, watertight to prevent ingress of rainwater, vermin-proof to prevent animals from entering the well (i.e. with no holes through which small mammals can enter), and lockable to prevent malicious (or curious) persons gaining access to the supply. Points of cable/wiring entry should have water tight seals. If ventilation is present ensure that it is also vermin-proof with appropriate wire mesh in place. http://publications.environment-agency.gov.uk/PDF/SCHO1000BFHB-B-E.pdf
D7 | Are the headworks completely sealed so that no surface water, spillages or vermin/insects can enter? | TBC - No risk | TBC | If the headworks are in an unsatisfactory state-of-repair then there is an increased risk of vermin entering or of surface flows inundating the structure. If there is evidence that the headworks are in an unsatisfactory state-of-repair then the likelihood score will be almost certain (value = 5). http://publications.environment-agency.gov.uk/PDF/SCHO1000BFHB-B-E.pdf
D8 | Are there land drains which channel water into the source? | TBC - No risk | TBC | Drainage systems, ditches, gulleys, channels, etc. can provide routes of ingress into water sources posing a risk of both microbiological and chemical contamination from surface water run-off. The likelihood score should take into account the probable time and extent to which the land is being grazed or subjected to agricultural applications. Mitigation might include diversion of the drainage arrangements or installation of appropriate treatment. Risks can be increased where the source is in a high vulnerability area ( see B1 Guidance).
D9 | Are there historic results from the supply confirming the radon levels are below 100Bq/l? | TBC - No risk | TBC | Where historic sample results for the supply are available, these should be a minimum of one year of monitoring data with seasonal variation. These should be used to support the risk assessment. If these indicate a low hazard ratings of source, <100Bq/l, analysis for radon is not required. The local authority can also request information on radon sample results and any waivers currently in place from the local public water supplier to inform this decision. Further information may be found in DWI guidance: http://www.dwi.gov.uk/stakeholders/guidance-and-codes-of-practice/pws-radon-QA.pdf
D10 | Does the local water company have a waiver for radon for abstraction points in the same aquifer? | TBC - No risk | TBC | Water companies are obliged to undertake monitoring for radioactive substances in moderate and high hazard sources according to the AEA Ricardo report. Where the results confirmed that the levels were unlikely to exceed 100Bq/l, they were encouraged to apply for notices exempting them from further radon monitoring. Ask the local water company for information relating to radon waivers for sources in the same aquifer if present, and request sample results for this. If sample results have been obtained from a similar aquifer over a year period and are below 100Bq/l, this should inform your risk assessment as to whether monitoring of the private source is required. Further information may be found in DWI guidance: http://www.dwi.gov.uk/stakeholders/guidance-and-codes-of-practice/pws-radon-QA.pdf
D11 | Do radon-in-air measurements confirm the levels are below 200Bq/m3 (where there is no existing radon treatment)? | TBC - No risk | TBC | Where radon levels in air are below 200Bq/m3, there is no requirement to undertake analysis for radon in water. Where radon levels in air exceed 200 Bq/m3 , installation of treatment may be required. Consideration should be given to any health issues experienced by residents living in the property when making a decision using information provided in PHE guidance on radon in homes: http://www.ukradon.org/
D12 | Does the PHE report or AEA Ricardo report identify the site as moderate or high hazards rating? | TBC - No risk | TBC | Information provided in these reports identify where a source is considered to be a moderate or high hazard rating for naturally occurring radon. If there is no treatment in place for radon, the local authority should consider undertaking radon in air sampling as part of the investigation. However, where there is treatment in place and the site is still considered to be moderate or high risk, radon in water analysis should be undertaken. Identify what control measures are already in place for dealing with radon. Identify what/where the source of radon is from and undertake analysis for the relevant radionuclides associated with this source. Information on this can be found in the EA Radionulides handbook: https://www.gov.uk/government/uploads/system/uploads/attachment_data/file/291128/sp3-101-sp1b-e-e.pdf Also, refer to PHE for further guidance.
D13 | Do sample results indicate radon levels are greater than 1000Bq/l? | TBC - No risk | TBC | The Euratom and Private Water Supply Regulations require that remedial action is taken if 1000Bq/l is exceeded. Where sample results indicate radon levels >1000Bq/l, a Regulation 18 notice should be issued and identification of any treatment available and in use. If not, treatment will be required. PHE should be consulted to determine if it is a risk to health or not (i.e. if a Reg 18 or section 80 notice is required). Contact PHE for further guidance and information on remedial works to reduce radon:- https://www.gov.uk/government/publications/uk-recovery-handbooks-for-radiation-incidents-2015 and http://dwi.defra.gov.uk/private-water-supply/RHmenu/Updated%20Manual%20on%20Treatment%20for%20Small%20Supplies.pdf
D14 | Is the source exposed to risks of faecal contamination from wildlife | TBC - No risk | TBC | Any evidence of wildlife, mammals (rabbits, deer, etc.), birds (gulls, geese, migratory birds, etc) reptiles ( frogs, newts, etc) at the source could indicate the potential for contamination of the supply either from faecal material or from carcasses falling into the supply. Measures required to mitigate risks from wildlife should take into account the type and extent of risk presented. The occurrence of wildlife might be transient (e.g. from birds overhead) or more regular, where for example, the source is in close proximity to rabbit warrens.
D15 | 0 | N/A - No risk |  | No guidance available
D16 | 0 | N/A - No risk |  | No guidance available
D17 | 0 | N/A - No risk |  | No guidance available
Section E - SOURCE: Mains water supplied by means of pipes (Regulation 8 supplies)
E1 | Is there evidence the supply main is coal tar lined? | TBC - No risk | TBC | Coal tar was used pre-1970 to line iron mains to protect them from corrosion. This material contains compounds, amongst others, called polycyclic aromatic hydrocarbons, some of which are known to be carcinogenic above certain concentrations (consult WHO guidelines). Furthermore, coal tar lining can cause various unpleasant aesthetic issues, including petrochemical like taste and odours. Positive evidence for the presence of coal-tar linings may be the analytical results for PAH's or reports of taste and odour. Checks can be made via water company websites for failures of these parameters. In addition, checks can be made with the water company to determine any recorded coal tar lined mains, and whether the local area was relined as part of its renovation programme. If there is any positive evidence of the presence of coal-tar linings, the water company can confirm any existing control measures and any planned long term remediation. In the absence of any positive evidence, score the likelihood as 1.
E2 | Are there sediments in the main? | TBC - No risk | TBC | Sediment in mains may be present as particles of iron, manganese and aluminium caused by the corrosion of cast iron mains or when these have not been removed effectively by treatment. When sediments are mobilised they cause transient aesthetic issues. Failures of iron, manganese and turbidity can be checked through water company websites. In addition, checks can be made with the water company to determine the number of consumers who reported discolouration in the supply area within the last 12 months.
E3 | Is the section of main upstream of the point of supply subject to good turnover of water (e.g. are there connections to properties nearby which would ensure the water is refreshed in the main constantly)? | TBC - No risk | TBC | Water that remains standing due to a lack of demand or throughput of water for any reason will stagnate over time causing the water quality to deteriorate. Surges of demand downstream, and notably where there is a sudden downstream drop in pressure will pull this poor water quality into supply leading to aesthetic issues. Consult with the water company to determine if there is evidence of poor turnover through taste and odour breaches or complaints, discolouration issues or detection of microbiological indicators such as coliform failures or elevated colony counts. In the absence of positive evidence of poor turnover, score the likelihood as 1.
E4 | If the area feeding the supply has had water quality related complaints in the last 12 months, have the causes been mitigated? | TBC - No risk | TBC | Checks can be made with the relevant water company to determine if there have been higher than average numbers of complaints in the local area in the last 12 months, and if so whether the cause has been identified and remediated.
E5 | Have any chemical parameters exceeded the standard in the previous 12 months in the mains supply? | TBC - No risk | TBC | Water companies are duty bound to comply with the Water Supply (Water Quality) Regulations 2000 (as amended) and supply water that is wholesome, as defined by those regulations. The Water Company is also duty bound to monitor its supplies to demonstrate to the DWI that it complies with the regulations. The information/data provided by this monitoring is made available to the general public, usually via company websites. This should be consulted to provide assurance that the supply has been consistently wholesome for 12 months prior to the risk assessment. The company may also have notices, undertakings or authorised departures on this supply specifying improvement works to achieve a wholesome supply. Where these are in place, confirm what remedial action is required and when it will be delivered.
E6 | Are there backflow protection deficiencies at any upstream industrial or commercial premises? | TBC - No risk | TBC | Chemical or microbiological contamination from upstream industrial and/or certain types of commercial activities such as printers, manufacturing businesses, dry cleaners, abattoirs, etc. can occur where there is a lack of, or inadequate, protection against the back-siphonage of contaminated water where compliance with the Water Supply (Fittings) Regulations has not been met. Check with the water company whether any current backflow protection deficiencies have been identified at any upstream commercial/industrial premises through their water fittings inspections programme.
E7 | 0 | N/A - No risk |  | No guidance available
E8 | 0 | N/A - No risk |  | No guidance available
E9 | 0 | N/A - No risk |  | No guidance available
Section F - This section has been left blank intentionally.
F1 | Is the supplier/contractor competent to undertake the requirements of BS 8551 - Provision and management of temporary supplies and distribution networks.? | N/A - No risk |  | BS 8551 is the code of practice for the provision and management of temporary supplies and distribution networks. Adherence to this code of practice provides assurance that required standards to prevent any contamination are met. Written confirmation that the supplier is following this code of practice must be demonstrated to reduce the risk of contamination.
F2 | Is the tanker suitable in accordance with BS 8551? | N/A - No risk |  | The tanker should be suitable for use to contain and deliver a wholesome supply. It should be robust, vandal proof, and in a general state of good repair. The tanker should comply with Regulation 5 of the Private water Supplies Regulations (e.g. WRAS approved). The use of the tanker for supplying drinking water should be carried out in accordance with the specifications of BS 8551, which includes requirements for cleaning, disinfection, filling of tanker or water bowser, and sampling.
F3 | Has the tanker been used exclusively for water (i.e. not previously used for milk)? | N/A - No risk |  | Any storage facility used previously for any other liquid presents a potential risk to human health. Containers which have previously contained milk are difficult to clean - steam cleaning of metal containers can result in organic matter and bacteria becoming baked on to the internal surface, and later breaking down into the water. If they have been used for anything other than water they must provide evidence that the tanker has been adequately cleaned prior to disinfection. Those previously used for milk or glucose should be avoided.
F4 | Has the tanker been cleaned and disinfected as specified in BS 8551? | N/A - No risk |  | BS 8551 is the code of practice for the provision and management of temporary supplies and distribution networks. Adherence to this code of practice provides assurance that required standards to prevent any contamination are met. Written records to show that the relevant steps have been followed must be provided.
F5 | Are records available to demonstrate activities have been undertaken in accordance with BS 8551? | N/A - No risk |  | BS 8551 is the code of practice for the provision and management of temporary supplies and distribution networks. Adherence to this code of practice provides assurance that required standards to prevent any contamination are met. The water service provider must provide evidence that the source water is wholesome in accordance with BS8551, stating the origin and description of the source water.
F6 | 0 | N/A - No risk |  | No guidance available
F7 | 0 | N/A - No risk |  | No guidance available
F8 | 0 | N/A - No risk |  | No guidance available
Section G - This section has been left blank intentionally.
G1 | Does the supplier/contractor operate in accordance with BS 8551? | N/A - No risk |  | BS 8551 is the code of practice for the provision and management of temporary supplies and distribution networks. Adherence to this code of practice provides assurance that required standards to prevent any contamination are met. Written evidence that the supplier is following this code of practice must be provided to confirm any contamination risks are reduced.
G2 | Is the temporary water storage facility suitable in accordance with BS 8551? | N/A - No risk |  | Storage facilities can comprise tankers, static tanks, bowsers, pillow tanks, etc. and the code of practice specifies which are appropriate and how they should be deployed. Documentation should be provided to confirm this.
G3 | Has the temporary water storage facility previously been used exclusively for water (i.e. not previously used for milk)? | N/A - No risk |  | Any storage facility used previously for any other liquid presents a potential risk to human health. Containers which have previously contained milk are difficult to clean - steam cleaning of metal containers can result in organic matter and bacteria becoming baked on to the internal surface, and later breaking down into the water. If they have been used for anything other than water they must provide evidence that the tanker has been adequately cleaned prior to disinfection. Those previously used for milk or glucose should be avoided.
G4 | Has the temporary water storage facility been cleaned and disinfected as specified in BS 8551? | N/A - No risk |  | BS 8551 is the code of practice for the provision and management of temporary supplies and distribution networks. Adherence to this code of practice provides assurance that required standards to prevent any contamination are met. Request evidence that the required steps have been followed to confirm this.
G5 | Does the source water originate from a wholesome supply i.e. a wholesome mains water/borehole/well/spring? | N/A - No risk |  | The water service provider must confirm the requirements of BS8551 have been met, in respect of the wholesomeness of the source water. Details of the source and evidence of its quality should be provided.
G6 | 0 | N/A - No risk |  | No guidance available
G7 | 0 | N/A - No risk |  | No guidance available
G8 | 0 | N/A - No risk |  | No guidance available
Section H - This section has been left blank intentionally.
H1 | Are the hoses used for filling clean, and suitable according to BS8551? | N/A - No risk |  | BS 8551 is the code of practice for the provision and management of temporary supplies and distribution networks. Adherence to this code of practice provides assurance that required standards to prevent any contamination are met. Hoses that are not suitable pose a risk of contamination. Request evidence that the required steps have been followed to confirm this.
H2 | Are the hoses used for filling stored off the ground on a reel and capped off? | N/A - No risk |  | Hoses that are not appropriately stored and/or are stored uncapped present a risk of contamination from the surrounding environment by various means including those posed by vermin or unclean ground conditions. They must be stored on a reel that is placed on a robust platform ensuring that it is clear of the ground. Pipe ends must be suitably and securely capped.
H3 | Are the outlets of the tank or tanker protected (bagged) and sealed? | N/A - No risk |  | Protecting the inlets and outlets of the tanks using, for example, plastic bags helps reduce the risk of contamination while in transit or during deployment.
H4 | 0 | N/A - No risk |  | No guidance available
H5 | 0 | N/A - No risk |  | No guidance available
Section I - SOURCE: Rainwater harvesting
I1 | Is there any protection against faecal or chemical contamination e.g. from wildlife or industrial emissions? | TBC - No risk | TBC | Rainwater contains traces of atmospheric and environmental pollutants and will be exposed to animal and bird faecal matter as it runs off the rooves. The extent of the contamination will vary from site to site but it is surfaces that offer the highest risk in terms of water contamination. e.g. if there are heavy industrial processes nearby, this can be the source of atmospheric pollutants. Therefore all rainwater harvesting systems are high risk and need specific protection against chemical and microbiological contaminates.
I2 | Are there any screens to prevent material entering the collection chamber (e.g. leaves, insects, twigs)? | TBC - No risk | TBC | Leaves, twigs and organic matter can enter the collection chamber or pipework, causing blockages and, if allowed to deteriorate, the build up of sludge in tanks and pipes. This can provide nutrients for micro-organisms, together with turbid water. Simple particulate filters or screens of a suitable mesh size positioned on guttering and at the intake to the collection chamber can be effective, and regular cleaning of screens is required.
I3 | Are there any trees overhanging the roof? | TBC - No risk | TBC | Overhanging trees can increase the quantity of leaves, twigs and organic matter filling and blocking any screens or filters. In addition overhanging trees provide habitat for birds, increasing the faecal loading on the roof. Branches overhanging the roof may be trimmed to minimise this hazard.
I4 | Is there evidence of lead, tin, copper, asphalt, new galvanised sheeting or wood preservatives on the roof? | TBC - No risk | TBC | Water collected from rooves will be subject to contamination by lead, tin, copper, asphalt, zinc or hydrocarbons depending on the nature and extent of the roof materials. The likelihood score should be based on the surface area covered by any of these materials.
I5 | Is there a bypass mechanism to exclude the first flush of rainwater from the roof? | TBC - No risk | TBC | A bypass mechanism which excludes the first flush of rainwater from the roof is beneficial because during dry periods the roof surface will accumulate dirt, faecal matter, organics, pollutants, etc, which will be concentrated into the first burst of rainfall which hits the roof and runs off into the rainwater harvesting system. If this first flush of rainwater is discarded the highly contaminated water will not enter the supply.
I6 | Is there adequate backflow protection for any rainwater harvesting systems in place at any of the properties? | TBC - No risk | TBC | Rainwater harvesting systems as a drinking water source may be augmented or backed up with other drinking water supplies. There are guidelines about their installation to ensure that there is no risk of contaminating any other drinking water supplies to the property (see BS 8515 - Rainwater harvesting systems Code of Practice). Where a rainwater harvesting system is installed, the pipework should be clearly labelled, and there should be an air gap (or other suitable backflow protection) between it and any other water source. Where a property also has a public water supply these requirements are covered by the Water Fittings Regulations 1999, which the local water undertaker has a duty to enforce.
I7 | 0 | N/A - No risk |  | No guidance available
I8 | 0 | N/A - No risk |  | No guidance available
I9 | 0 | N/A - No risk |  | No guidance available
Section J - SOURCE: Surface Water Intake (excluding springs)
J1 | Does the water quality vary at the intake point due to streaming/stratification/algal blooms/increased turbidity? | TBC - No risk | TBC | Where possible the intake should be located to ensure minimal variation in raw water quality. Where this is not the case the supply may be vulnerable to unexpected changes such as increased turbidity during heavy rainfall which may affect the efficacy of any subsequent treatment. Other factors affecting raw water quality include stratification, algal blooms or streaming. Streaming is where water short-circuits across a body of water; if contaminated any dilution effect will be reduced.
J2 | Are there screens in place at the intake? | TBC - No risk | TBC | Intakes should generally be protected by screens which remove weeds and debris from the raw water and prevent access by larger fish and vermin.
J3 | Where screens are present, is there a mechanism to remove debris? | TBC - No risk | TBC | A build up of debris on intake screens reduce flow and may cause a deterioration in the quality of the water supply. Screens therefore need to be cleaned by mechanical or manual means. Screens should also be suitably sized and located to provide maximum protection. Ask the site representative (owner/operator) for details of who is responsible for checking the screens and how often. Check any records available.
J4 | Does sediment build up inside the chamber and pipework after the intake point? | TBC - No risk | TBC | Surface water is very susceptible to sludge/sediment build up due to the exposed nature of the source to the environment. Therefore settlement chambers after the intake points are useful to allow suspended particles to settle out. However the outlet of the chamber should be raised to prevent otherwise settled material access to the rest of the supply system. Check the mechanism to empty the settlement chamber (drained down or periodically suctioned out) and ask how often this is done. Over time the chamber will fill with sediment which can spill over into the water supply (causing turbid water - which will be unacceptable to consumers or may impact on any available treatment such as UV). Like all tanks it should be constructed of materials that will not adversely affect water quality and be designed to prevent unauthorised access or entry of vermin.
J5 | Is there adequate protection of the intake point from livestock and wildlife? | TBC - No risk | TBC | If vulnerable to wildlife and livestock the intake must be adequately protected to prevent disturbance of sediment and deposits, which could enter the supply.
J6 | Does the availability of the water at the intake vary? | TBC - No risk | TBC | If this occurs, there is also the potential for insufficiency. Changes in levels and flows can result in deterioration of raw water quality causing increases in turbidity and colour due to the suspension of sediment. This will be most prevalent during periods of heavy rainfall, when flooding and rapid runoff of surface water into the source can occur, but this can also be in period of drought. Appropriate water treatment must be in place to meet the demands of these "flashy" conditions.
J7 | 0 | N/A - No risk |  | No guidance available
J8 | 0 | N/A - No risk |  | No guidance available
J9 | 0 | N/A - No risk |  | No guidance available
Section K - SOURCE: Water Storage (prior to treatment)
K1 | Is there a regular turn over of water? | TBC - No risk | TBC | The size of the tank should be proportional to demand. Water which remains standing for any length of time in a holding structure will deteriorate to varying degrees depending on the conditions it is exposed to. The level of the water within the reservoir/tank should therefore rise and fall at intervals throughout each day facilitating the constant input of fresh water to the structure. As a guide in raw water storage tanks, the water should be turned over (replenished due to use) every 7 days to avoid taste and odour issues and microbial or biofilm growth. Ask the owner to what extent the water is used on a daily basis and whether the capacity matches the demand, i.e. If the tank is too small then there may be a risk of insufficiency or if the tank is too large water may stand for long periods due to low demand.
K2 | Are the storage tanks vulnerable to ingress, flooding or other microbial contamination (e.g. wildlife access)? | TBC - No risk | TBC | The level of protection for all intermediate tanks or similar structures should be equivalent to that recommended for the source itself as the potential for contamination to enter the system via such intermediate points is just as high as for the source itself.
K3 | Is there a stock-proof fence around any inspection chambers? | TBC - No risk | TBC | Inspection chambers must be adequately protected by fences that are of appropriate height, material and robustness
K4 | Are the tanks regularly maintained to preserve their structural integrity and cleaned? | TBC - No risk | TBC | Verbal assurance from the owner that a reservoir is regularly cleaned/maintained is not evidence in itself that the action is undertaken or that the frequency is appropriate. Examine any available records, such as log books and/or supporting documentation such as contractual work receipts as evidence and in addition look for physical signs that covers and access points are in regular use for this purpose.
K5 | Are the storage tanks adequately protected against vandalism? | TBC - No risk | TBC | Tanks should be adequately protected against the risk of intentional damage. Covers and access points must be securely locked when not in use and access to these points controlled. Check that the owner has records of all key owners. The reservoir/tank should be suitably robust in structure in a secure location.
K6 | Is the cleaning regime for the tank appropriate? | TBC - No risk | TBC | Sediment and sludge build up is expected, but should be minimised through the design and operation of the tank including maintenance activities. Appropriate cleaning means sufficient cleaning to prevent sediment or sludge build up, before it causes microbiological growth or aesthetic risk.
K7 | 0 | N/A - No risk |  | No guidance available
K8 | 0 | N/A - No risk |  | No guidance available
K9 | 0 | N/A - No risk |  | No guidance available
Section L - TREATMENT PLANT: Plant Design (i.e. excluding point of use devices in dwellings or premises)
L1 | Is there adequate Cryptosporidium treatment in place? | TBC - No risk | TBC | Found in faecal matter such as from livestock, wildlife and in sewage, Cryptosporidium can affect any surface water sources or vulnerable ground water sources influenced by surface water. A multi-barrier approach is recommended to remove Cryptosporidium from supplies; coagulation, clarification and filtration for example. Chlorination is not effective against Cryptosporidium, however, UV treatment will inactivate it.
L2 | Is the treatment plant operating within the design capacity? | TBC - No risk | TBC | For any treatment process there are operational limits beyond which treatment performance diminishes. The quality of the drinking water being produced may be adversely affected if this occurs. Therefore any process being used beyond its designed capacity or specification requires action to be taken. Refer to any available information provided by the manufacturer on the design specification for the treatment and criteria on which the treatment process was designed. Check whether the 'demand' on the supply has significantly increased since the plant was designed and built e.g. additional commercial premises, large numbers of additional houses. Check the volume of water being treated and the type of treatment process. Flows greater than design capacity will compromise water quality, due to insufficient contact time with UV or overloading of filters for example.
L3 | Is it possible to by-pass any stage of treatment? | TBC - No risk | TBC | Check for pipe work and/or valves that by-pass any treatment stage. If a UV lamp can be easily switched off (e.g. to save electricity) this is bypassing a treatment stage.
L4 | Where there is a blending facility, is there an appropriate blending strategy? | TBC - No risk | TBC | Blending can be the mixing of a public water supply with a private supply or between multiple private water sources. This may be carried out to meet water quality standards. Assessment of the blending strategy requires interpretation of sample results and knowledge of seasonal variations e.g. of boron, arsenic, fluoride and nitrates. Check that procedures are in place for the calculation and management of the blending ratio. I.e. are the sources being blended in the correctly quantities to meet the criteria defined in procedures to eliminate exceedances of the standards? Does the strategy take into account seasonal variations?
L5 | Are there frequent flow variations through the treatment plant, which render the treatment process inadequate? | TBC - No risk | TBC | Variation in flow rates can cause low pressure, insufficient or loss of supply to properties. Flow variations may also compromise water quality by affecting coagulation, clarification, filtration and disinfection treatment processes, particularly when sudden changes occur. Changes to flow rates should therefore be made gradually and should not exceed the design capacity of any individual treatment process.
L6 | Are there frequent demand variations, which could cause insufficiency? | TBC - No risk | TBC | Check whether properties or draw-off points fed by the supply ever run out of water. Treated water storage tanks can be used to help balance fluctuations in demand. Alternatively actions can be taken in the downstream network to reduce demand such as water efficiency measures.
L7 | 0 | N/A - No risk |  | No guidance available
L8 | 0 | N/A - No risk |  | No guidance available
L9 | 0 | N/A - No risk |  | No guidance available
Section M - TREATMENT PLANT: Filter beds (sand, anthracite, etc)
M1 | Is there adequate pre-treatment (e.g. clarification) in place if required? | TBC - No risk | TBC | Filtration may be preceded by clarification processes dependant on the quality of the source water and corresponding design of the treatment works. Clarification by coagulation is typically installed to remove the majority of colour and turbidity from the raw water. Evidence of the requirement for pre-treatment or of inadequate pre-treatment is an increased frequency of filter blocking or backwashes being required.
M2 | Is there adequate process control for filtration (e.g. turbidity monitors)? | TBC - No risk | TBC | Filter performance may be determined using turbidity monitors - ideally on the outlet of each filter. Where filtered water turbidity is higher than 1.0NTU or where this value is frequently approached then action is needed to improve filter performance and/or any preceding treatment processes. A typical filter cycle will show increased turbidity at the start and end of the cycle (after commissioning and prior to backwashing or refurbishment); these are normal and should be managed operationally.
M3 | Can the filters overload? | TBC - No risk | TBC | Check that the filters are managed so they cannot overload; the number of filters should be appropriate to the volume of water being processed. The operator should ensure that the incoming water isevenly distributed across all filters.
M4 | Do the filters block? | TBC - No risk | TBC | Confirm whether the operator checks the filters e.g the surface should appear an even colour, they should be monitored for headloss and turbidity. Determine the regularity of these checks, and of backwashes and media replacement.
M5 | Is the media depth at a minimum to design specification? | TBC - No risk | TBC | Confirm with the person responsible for maintenance how they check media depth and ensure minimum depth is maintained as per the manufacturer's specification.
M6 | Is the filter media composition as per design specification? | TBC - No risk | TBC | Confirm with the person responsible for maintenance whether the media composition is per the manufacturer's specification.
M7 | Is the backwashing regime operated to the design manual (including cycle length, uneven scour, pump failure, loss of filter media) | TBC - No risk | TBC | Filters are cleaned by the process of backwashing which is typically triggered by filter headloss or increased turbidity of the filtered water. Operators should observe the entire backwash process for each filter for signs of problems such as; uneven bed surface, cracked surface, uneven airscour pattern, presence of vegetation/plants, media loss, effectiveness of wash and wash times. Check with the operator and the documented procedures to determine the criteria for initiating backwashes. Determine whether an appropriate procedure adn records exist that such observations are being made regularly.
M8 | Do the filters appear well maintained? | TBC - No risk | TBC | Check the general structural condition of filters for major issues and confirm the maintenance regime.
M9 | Does the water run to waste when rapid gravity filters are started up? | TBC - No risk | TBC | Ask the person responsible for maintenance, if the filters can be run to waste on start up to prevent potentially inadequately filtered water entering the supply.
M10 | Can the filters be started up gradually (i.e. not immediately run at full capacity)? | TBC - No risk | TBC | During the early phases of a filter cycle the turbidity of the filtered water will be high. Slowly starting the filters, gradually increasing the flow is a means of minimising the impact of this stage on the quality of the drinking water being produced.
M11 | Where Cryptosporidium is potentially present in the raw water, is a turbidity of less than 1.0 NTU achieved in the filtered water? | TBC - No risk | TBC | A well operated filter provides a good barrier against Cryptosporidium. Filtered water should have a turbidity well below the 1NTU required prior to disinfection.
M12 | Is the backwash water recycled to head of works? | TBC - No risk | TBC | Backwash water will contain debris washed out of the filter media during cleaning including microbial contaminants such as algae and Cryptosporidium. Ideally backwash water is run to waste or into tanks for disposal. However, this water may be pumped back to the start of the treatment process. Due to the nature and concentration of the contaminants present, the reuse of backwash water should be appropriately controlled to prevent its reuse under certain conditions (high turbidity). Check with the operator whether such controls are in place.
M13 | Is algal growth apparent in/on filters? | TBC - No risk | TBC | Some algal and weed growth on slow sand filters is normal . It is only problematic if the growth becomes excessive.
M14 | For slow sand filters, is the required ripening period adhered to before putting the water into supply? | TBC - No risk | TBC | A new biological layer, or Schmutzdecke, will form between 2 days and 2 weeks after the filter is back in operation. This layer is crucial to the effectiveness of the filter, and therefore until it has established, the filtered water should be returned to the start of the treatment process or discarded as it will not have been adequately treated.
M15 | 0 | N/A - No risk |  | No guidance available
M16 | 0 | N/A - No risk |  | No guidance available
Section N - TREATMENT PLANT: Granular Activated Carbon (GAC) filters
N1 | Has the GAC been installed as per the design specification? | TBC - No risk | TBC | Granular activated carbon (GAC) is used when removal of organic compounds (such as pesticides) is necessary. GAC is used in a number of ways; a layer can be incorporated into a conventional sand filter (to make a dual media filter); it may replace the sand filter stage or be used after the sand filtration stage. The design of the GAC adsorbers should be based on source water characteristics.
N2 | Is the GAC design appropriate for the nature of the raw water quality? | TBC - No risk | TBC | GAC is used to remove many types of organic compounds, including the majority of pesticides. However, there are several forms of GAC and the selection of the most suitable form is mostly dependant on its ability to remove the specific organic compounds to be reduced or removed. Check the type and grade and its intended application with the manufacturers product specification.
N3 | Is the media depth and composition appropriate for the nature of the raw water quality? | TBC - No risk | TBC | Checks should be made to ensure an adequate amount of media is maintained in each filter. This is usually achieved by regularly measuring the filter bed depth which will highlight any loss of media over time. Determine whether this activity being carried out and what do the records show if it is being carried out. If there is evidence that media is being lost then action will be required to prevent further loss either by redesigning the filter and or modifying the backwash process. Ask the operator how they check media composition depth and what triggers media replacement. Limited air scouring is used when backwashing GAC filters to prevent media loss.
N4 | Is the plant regularly operated and maintained according to the design specification? | TBC - No risk | TBC | GAC has an adsorption capacity and its ability to remove organic compounds expires once the surface of the carbon is saturated with organic compounds. At this point, the carbon will either need to be replaced or regenerated. Without this maintenance, the filter is no longer effective as an adsorber - its principal purpose. Check maintenance records and establish if these activities are being carried out according to recommended frequency.
N5 | 0 | N/A - No risk |  | No guidance available
N6 | 0 | N/A - No risk |  | No guidance available
N7 | 0 | N/A - No risk |  | No guidance available
Section O - TREATMENT PLANT: Ion Exchange (may be used for nitrate, arsenic or manganese removal etc.)
O1 | Is the treatment plant operating within its design capacity? | TBC - No risk | TBC | For any treatment process there are operational limits beyond which treatment performance diminishes. The quality of the drinking water being produced may be adversely affected if this occurs. Therefore any process being used beyond its designed capacity or specification requires action to be taken. Refer to any available information provided by the manufacturer on the design specification for the treatment and criteria on which the treatment process was designed. Check whether the 'demand' on the supply has significantly increased since the plant was designed and built e.g. additional commercial premises, large numbers of additional houses. Check the volume of water being treated and the type of treatment process. Flows greater than design capacity will compromise water quality, due to insufficient contact time with UV or overloading of filters for example. If unclear ask the owner of the supply to verify the information from the installer or supplier.
O2 | Is there adequate pre-treatment (e.g. filtration) in place if required? | TBC - No risk | TBC | Ion exchange is usually preceded by filtration dependant on the quality of the source water and corresponding design of the treatment works. This should remove particulates from the raw water to prevent the media blocking. Evidence of the requirement for pre-treatment or of inadequate pre-treatment is an increased frequency of filter blocking or backwashes being required.
O3 | Is the media depth at a minimum to design specification? | TBC - No risk | TBC | Confirm with the person responsible for maintenance how they check media depth ( during initial filling and replacing/ toping up the media) and ensure minimum depth is maintained as per the manufacturer's specification.
O4 | Is the ion exchange media composition as per design specification? | TBC - No risk | TBC | Confirm with the person responsible for maintenance whether they understand what the media composition is and whether this was to the manufacturer's specification.
O5 | Is there a suitable maintenance schedule? | TBC - No risk | TBC | Ion exchange units will needs periodic maintenance as specified by the manufacturer. The operator should maintain records to confirm this is being adhered to.
O6 | Is the regeneration regime as per design specification? | TBC - No risk | TBC | Ion exchange units are either cation exchangers that exchange positively charged ions (cations) or anion exchangers that exchange negatively charged ions (anions). These ions need to be replaced periodically by flushing the resin with a solution containing an excess of these ions – typically brine solution containing sodium ions. The frequency will be specified by the manufacturer. The rate at which the operator uses and has to buy fresh solution may be an indication as to whether this regeneration regime is being adhered to.
Section P - TREATMENT PLANT: Other Filters
P1 | Does the plant design take into account the raw water quality? | TBC - No risk | TBC | The raw water quality at each site will determine the required design of the membrane plant depending on the nature of the water quality challenge. The manufacturer will recommend specific design characteristics and pore sizes for the membranes to remove specific chemical or microbiological contaminants. Ask for evidence that the membrane plant is site-specific.
P2 | Is there adequate pre-treatment to prevent membrane fouling and damage? | TBC - No risk | TBC | The integrity of the membrane is critical to ensure effective treatment. Therefore the presence of an appropriate pre-treatment is essential to protect the membrane against chemical (e.g. salinity), microbiological, aesthetic contamination or insufficiency of the supply . Pre-treatment must be adequate to prevent fouling and scaling, as well as protecting the membranes from physical damage. There should be suitable protection/screens to neutralise pretreatment oxidants and the operator should provide procedures and records of the operation and monitoring of the membrane to check for integrity. Records should also be kept when membranes are replaced, including when ruptured or damaged. Ask the owner to demonstrate, with suitable documentation that the pre-treatment is adequate. For further information please contact DWI.
P3 | Are the cleaning regimes (for descaling and antifouling, etc.) being followed as set out in the design specification? | TBC - No risk | TBC | Check the membrane's design manual requirements for specification of the cleaning (antifouling and descaling) regime. The operator should provide evidence to demonstrate compliance with this manual. For further information please contact DWI.
P4 | Are the chemicals used in the process as recommended by the manufacturer? | TBC - No risk | TBC | Any chemicals used in the treatment stage should be specified by the manufacturer and the operator should be asked for evidence that the correct chemicals are in use. Incorrect chemicals could cause membrane damage. For further information please contact DWI.
P5 | Is there a procedure to confirm that the integrity of the membrane is maintained? | TBC - No risk | TBC | The integrity of the membrane is critical to ensure effective treatment. There should be suitable protection/screens to neutralise pretreatment oxidants and the operator should be asked for evidence of how the membrane is checked for integrity. They should also keep records when a membrane is replaced when ruptured or damaged.
P6 | Are the filters replaced as per the manufacturer's specifications (or more frequently)? | TBC - No risk | TBC | The manufacturer will specify the frequency at which the filters should be replaced. Ask for evidence that this is being adhered to.
P7 | Was the raw water quality taken into account when the filters were installed? | TBC - No risk | TBC | The raw water quality on each supply will determine the filter type, number and size (e.g. 1 micron, 5 micron, etc) depending on the nature of the water quality challenge. The installer should specify this based on quality characteristics of the source water. Ask the owner of the supply if they have details of this specification.
P8 | 0 | N/A - No risk |  | No guidance available
P9 | 0 | N/A - No risk |  | No guidance available
Section Q - TREATMENT: Desalination or Reverse Osmosis
Q1 | Is there any likelihood of industrial, domestic or boating waste flows in the vicinity of the water intake to the desalination plant? | TBC - No risk | TBC | All surface waters, marine and estuarine waters will contain microbial and chemical contamination derived from human activity (industrial, recreational etc.). The location of the abstraction point is key to reducing the levels of such contaminants (including salinity) either by timing when water is drawn or by siting the abstraction point where levels of such contaminants are lower. Knowledge of potential contaminants is important.
Q2 | Could any chemical stores potentially contaminate the supply at the intake? | TBC - No risk | TBC | The hazards may be chemical or aesthetic (taste and odour) contamination. Identify any potential chemicals stored near the intake and their potential impact on the treatment process. Measures include moving intake points, restricting discharges of descaling or antifoaming chemicals, or moving chemical stores.
Q3 | Are there variations in source water levels, which affect the ability to abstract water? | TBC - No risk | TBC | Such variations may result in insufficiency of supply, and where such circumstances occur the person in control should ensure that alternative supplies or sources are available during these periods.
Q4 | Is there adequate treatment to prevent membrane fouling and damage? | TBC - No risk | TBC | Coagulation and micro-filtration pre-treatment are normally used to reduce the impact and fouling of the membranes by particles together with chlorination or biocides to eliminate microbial fouling of membranes. Ensure pretreatment is suitable and adequate to prevent fouling.
Q5 | Are oxidants removed during pretreatment? | TBC - No risk | TBC | Failure to remove oxidants during pretreatment can cause membrane damage. Ensure there is a suitable process to neutralise pretreatment oxidants; monitor membrane integrity and replace when ruptured or damaged
Q6 | Has the operator mitigated against the demineralisation of the water? | TBC - No risk | TBC | Water produced from reverse osmosis treatment is low in minerals and therefore aggressive to pipes, and the taste is unacceptable to consumers. It therefore needs to be remineralised which is normally achieved via blending with up to 10% of wholesome water. Evidence that this has not been achieved may be pipe corrosion (higher concentration of metals) or taste problems.
Q7 | Is the treated supply blended with other sources of drinking water in distribution? | TBC - No risk | TBC | Blending drinking water from different sources may give rise to water quality issues, such as high mineral levels or aesthetic properties and the water may be more aggressive to pipes. Supplies should be blended in a consistent manner to ensure, amongst other things, that consumer perception is not adversely affected by intermittent and variable blend ratios.
Q8 | Are the chemicals used in the process as recommended by the manufacturer? | TBC - No risk | TBC | Incorrect chemicals can result in less effective treatment or cleaning, or contamination. The person in control must use the chemicals recommended by the manufacturer and ensure they are within use-by dates.
Q9 | Is the plant design appropriate for the nature of the raw water quality? | TBC - No risk | TBC | The plant design must be capable of meeting the water quality challenges presented by the source water type it is required to treat, i.e. rainwater, seawater, other. Check the manufacturer's specification with the person in control/operator to verify that the treatment arrangements are suitable.
Q10 | 0 | N/A - No risk |  | No guidance available
Q11 | 0 | N/A - No risk |  | No guidance available
Q12 | 0 | N/A - No risk |  | No guidance available
Section R - TREATMENT PLANT: Disinfection: UV
R1 | Is there adequate preliminary treatment in place? | TBC - No risk | TBC | Check that the water passing the UV lamp is monitored for turbidity and that turbidity readings do not exceed the acceptable range for the lamp. Ensure that turbidity remains below 1NTU prior to disinfection. Chekc for any evidence of sediment and/or algae build up on the lamp sleeves.
R2 | Is there a validation certificate for the UV system? | TBC - No risk | TBC | A validation certificate issued on installation should be inspected. Ensure that the device remains effective against target pathogens and check that there have been no changes since the certificate was issued, for example changes in source water quality, flow and demand, number of premises supplied. The validity of the certificate should be challenged where conditions have changed since its installation.
R3 | Can water be supplied if the U.V. is not operational? | TBC - No risk | TBC | Where UV treatment is installed to mitigate against, for example, the risk of Cryptosporidium then the system should not be operable if the UV is not working. This may be achieved through failsafe mechanisms whereby the supply ceases if the UV stops working. If the UV treatment can be switched off, or bypassed, but water can still be delivered there is a risk that undisinfected water may be supplied. If the system is likely to occasionally shut down, some capacity to store treated water as contingency may be required.
R4 | Is the UV operating within its validated range for the product type or lamp? | TBC - No risk | TBC | Check the UV lamp manual and the specific range for the UV lamp. Can the operator demonstrate that it is operating within this range to address the source water quality challenges.
R5 | Is the equipment regularly maintained e.g. bulb replacement, cleaning? | TBC - No risk | TBC | Refer to the maintenance regime recommended by the manufacturer and ask for written documentation that this is being adhered to, including servicing, cleaning the unit and replacing the bulbs.
R6 | 0 | N/A - No risk |  | No guidance available
R7 | 0 | N/A - No risk |  | No guidance available
R8 | 0 | N/A - No risk |  | No guidance available
Section S - TREATMENT PLANT: Disinfection: chlorination
S1 | Is there a backup/standby system for automatic chlorine dosing or an automatic shutdown arrangement? | TBC - No risk | TBC | Automated chlorine dosing units may operate with a standby system in place, ensuring that chlorine is continued to be dosed at the appropriate level if the main chlorination system fails (for example if the supply runs out, or a dosing line blocks). This will help ensure water is subject to disinfection at all times.
S2 | Is there evidence that maintenance has been carried out of the disinfection system within the last 12 months? | TBC - No risk | TBC | Refer to the maintenance regime recommended by the manufacturer and ask for written documentation that this is being adhered to, including servicing. Such documentation includes entries in a log book, diary records, and full records.
S3 | Is there an appropriate alarm in the event of loss of chlorine dosing? | TBC - No risk | TBC | Determine what alarms are in place to alert the operator of any loss of chlorine dosing, and whether this is linked to any automatic shut down of the supply to prevent undisinfected water entering the supply.
S4 | Are the chemicals of drinking water grade i.e. approved for use in drinking water supplies? | TBC - No risk | TBC | Chemicals used in a chlorination system must be approved for use with drinking water supplies and comply with Regulation 5 of the PWS Regulations in England and its equivalent in Wales.
S5 | Is the existing dosing effective? | TBC - No risk | TBC | Adequate mixing, dosing levels and contact time are important factors for determining disinfection efficacy. Disinfection by-products should be minimised through control of dosing regimes.
S6 | 0 | N/A - No risk |  | No guidance available
S7 | 0 | N/A - No risk |  | No guidance available
S8 | 0 | N/A - No risk |  | No guidance available
Section T - TREATMENT PLANT: Other (answer for any treatment process)
T1 | Are all chemicals used for water treatment approved and in date? | TBC - No risk | TBC | Check all chemicals being used on site to ensure they comply with Regulation 5 and that they are within expiry date.
T2 | Are there controls in place for chemical deliveries to avoid chemicals being added to the wrong storage vessel? | TBC - No risk | TBC | Check how chemical deliveries are made and ensure there are controls in place to avoid mix up of chemicals e.g. check dosing points are unique, chemical deliveries are always accompanied by competent person, an approved chemical deliverer is employed, or that a chemical specification sheet accompanies any delivery.
T3 | Are chemical injection point(s) protected against potential damage e.g. covered, frost proofing, etc? | TBC - No risk | TBC | Ask for evidence as to how any dosing point is protected from extremes of weather of physical damage.
T4 | Are there procedures in place to ensure treatment is re-established after any loss of power supply? | TBC - No risk | TBC | Check there is an adequate procedure in place to restart treatment processes after loss of power, including checks of individual processes to ensure they are working within specification. Some processes such as biological filters may require a period of run to waste.
T5 | Is there a power back-up or alternative power supply? | TBC - No risk | TBC | Does the site have a back up generator that is sufficient to power up all the critical treatment processes? Where an alternate power supply is not present; what contingency is in place for the provision of alternate supplies of drinking water? See question Z12.
T6 | Is the treatment plant adequately protected against vandalism? | TBC - No risk | TBC | Check perimeter fencing, access gates and the control of the use of any security keys. Other security measures such as patrols and CCTV should be considered depending on the size of the supply.
T7 | Is the site liable to flooding which would result in loss or restriction of treatment process? | TBC - No risk | TBC | Gauge from surrounding topography if the site is at risk of flooding. Ask the person in control if the site has been flooded in the past. The Environment Agency provide information on flood zones via their and 'What's in my backyard?' website tool.
T8 | Could access to the plant be lost or restricted due to weather extremes or other events? | TBC - No risk | TBC | Gauge from topography and access routes if the site could become isolated during adverse weather. Ask the person in control if the site has been isolated in adverse weather conditions such as flooding or heavy snow. Lack of access during these times may mean essential water quality checks can not be made, or that chemicals stocks can not be replenished. For sites where access is difficult during periods of adverse weather there should be adequate procedures to manage stocks of treatment chemicals and communication with consumers should boil water advice be necessary.
T9 | Could adverse weather conditions render the treatment process and/or chemicals ineffective? | TBC - No risk | TBC | Cold weather can cause dosing lines to freeze and have a direct adverse impact on the efficacy of treatment processes. Pipes should be lagged where appropriate and equipment protected from frost / freezing. During periods of cold weather treatment processes should be checked and there should be adequate contingency procedures should pipes or processes fail. See question U3.
T10 | Are stored chemicals or oil adequately bunded? | TBC - No risk | TBC | Chemical storage should be contained in a bunded area sufficient to hold all the chemical compound in the event of a burst container. Check there are no drain holes in the bunding and that the containment area is not liable to fill with rain water. This can be a robust solid crate or tub if large enough.
T11 | 0 | N/A - No risk |  | No guidance available
T12 | 0 | N/A - No risk |  | No guidance available
T13 | 0 | N/A - No risk |  | No guidance available
Section U - TREATMENT: Monitoring. Use this section for all treatment systems
U1 | Are there appropriate online monitors? | TBC - No risk | TBC | On-line monitors should be appropriate to any treatment processes present. Where filtration is practiced or UV treatment is in place, turbidity monitors allow the operators to check that filtration is effective in reducing the turbidity levels, so that water presented for disinfection is below 1 NTU. If the supply is chlorinated, a chlorine monitor will ensure that the supply is maintaining the effective chlorine dose for disinfection. If appropriate manual checks are not carried out (with appropriate documentation), on line monitors or an equivalent system should be used.
U2 | Are they calibrated and maintained? | TBC - No risk | TBC | Most on-line monitors require regular calibration and occasional maintenance to ensure their measurements are accurate and the person in control of the supply can be assured that the process is operating within specification. The manufacturers should specify the frequency, but as a rule calibration with standards should be at least monthly. If this is carried out through a service agreement with the installer or other contractor, then you should confirm that the number of visits are appropriate and there is evidence the service agreement is being adhered to.
U3 | Do the on-line monitors have alarms? | TBC - No risk | TBC | This should be proportionate to the size of the supply - one with two or three domestic dwellings may not require alarms, but a supply with several properties including commercial premises should have alarms on the monitors. If they do, are the trigger levels appropriate? Turbidity on filtered water should alarm at 1NTU as above this any subsequent UV treatment will not be fully effective. If chlorine disinfection is practised, the operator should specify triggers for low or high dose which should alarm if breached to alert them to the fact that either the water is not being adequately disinfected, or that water is being supplied with high levels of chlorine, which may be unacceptable to the consumer. Check what action is taken if the alarm is triggered - is the response time appropriate and is there evidence the procedures are being adhered to. Is there an auto shutdown of the supply if disinfection fails? An auto shut down would be appropriate if no one could hear the alarm and it could not be acted on.
U4 | If monitors are not present on the supply, is any on-site testing being carried out? | TBC - No risk | TBC | If monitors are not present, or they are not linked to alarms, does the operator carry out any routine on-site tests. Typically this should be chlorine levels if chlorine disinfection is carried out, turbidity if filtration and/or UV treatment is in place. On-site testing should be carried out on a routine basis (daily to weekly at a minimum depending on the nature of the source, hazards in the catchment and the population served) and also on a reactive basis, for example if rainwater causes increased turbidity in the source water then additional monitoring should be carried out during and after periods of heavy rain. The extent of the monitoring depends on the nature of the raw water and the upstream distribution network.
U5 | Is there a basic schematic for the treatment and monitoring equipment? | TBC - No risk | TBC | This should at least include locations of the incoming water flow, direction of flow, bypass points, dosing points, treatment type and points, monitor locations, out flow, etc. and materials.
U6 | 0 | N/A - No risk |  | No guidance available
U7 | 0 | N/A - No risk |  | No guidance available
U8 | 0 | N/A - No risk |  | No guidance available
Section V - DISTRIBUTION: Distribution Network
V1 | After treatment is the water fully compliant with quality standards? | TBC - No risk | TBC | For a PDS this question is only relevant if additional treatment takes place after the point of entry from the public supply. For all other private supplies this can be determined by the examination of sample results, either taken during the risk assessment, during previous risk assessments or through other monitoring arrangements, e.g. EA ground water monitoring surveys, on-site tests. If results indicate that the water is not compliant with quality standards, the control measure(s) must be appropriate to the cause, as indicated by the results, and may require revision of the treatment.
V2 | Are there latrines, septic tanks, waste pipes, animal enclosures or cess pits present in the vicinity of the distribution system? | TBC - No risk | TBC | If unsewered human or animal sanitation is present within 50m of the distribution system then there is potential for raw human sewage to contaminate the distribution network if there are any defects. Consider any available information on the positioning of septic tanks as well as their condition (maintenance), as well as any available information on the soakaway location in relation to the distribution network. Similarly if there are pit latrines in use, e.g. at a campsite or areas where chemical toilets are discharged, confirm the location of the disposal point or latrine in relation to any clean water pipes.
V3 | Is there evidence of disinfection by-products in the network (e.g. taste problems due to THM's)? | TBC - No risk | TBC | There are many different disinfection by-products but the most commonly analysed-for one is Trihalomethanes (THMs) which is usually identified through sample results. In certain circumstances they may cause taste/odour complaints. This will only be applicable in a Private Distribution system if there is additional treatment after the point of supply and where chloramination or chlorination is present, and such an arrangement should be checked. The presence of THMs is linked to high levels of organic matter in the raw water and/or poor dosing controls during treatment.
V4 | If chlorine disinfection is practiced is there a disinfectant residual in the distribution network? | TBC - No risk | TBC | If chlorine disinfection is practised, determine chlorine residuals through on-site tests. For a private distribution system there may be a residual disinfectant in the network. Answer 'yes' to this question if at least 0.2mg/l is present.
V5 | Is there a suitable written procedure for mains repair and maintenance? | TBC - No risk | TBC | Relates to the existence of a procedure and how well it ensures protection against contamination i.e. hygienic operations (repairs being carried in a clean environment, fittings disinfected before use, etc.). If no, the likelihood score relates to the frequency of mains repair or other maintenance.
V6 | Is there history of any fractures or faults in the distribution system which could allow ingress of contamination? | TBC - No risk | TBC | A history of fractures or faults (burst pipes, loss of supplies) could indicate that the pipework is in an unsatisfactory condition or is vulnerable to damage. In a pumped supply this may indicate a lack of pressure control resulting in leaking pipes. Other indicators of existing leaks may be lower than expected chlorine residuals (on a chlorinated supply), high plate counts or other microbial indicators although these may be absent as under normal (pressurised) conditions ingress will not occur.
V7 | Is there any other route by which contamination can enter the distribution network via back-flow? If there is ponding of surface water or poor drainage, could water be pulled into the system during low pressure or changes in pressure, e.g. backflow from hoses, taps, or standpipes? | TBC - No risk | TBC | Contamination can also enter the distribution network via back-flow. This comprises back pressure (pushed) or back-siphonage (sucked). Where pressure differentials occur without suitable back-flow or air gap protection then contamination may enter the network through cross connections; leaking joints, broken pipes etc. Back-flow and other suitable fittings (including air gap protection) should be installed on animal watering troughs, standpipes, hoses, commercial premises, for example. If the drinking water is originally from a public supply (i.e. to a PDS or temporary event) the relevant water company or licensee will have responsibility for the enforcement of the Water Fitting Regulations 1999 and should be consulted if any cross connections, back-siphonage and back-flow hazards are identified.
V8 | Is there evidence any pipes are coal tar lined? | TBC - No risk | TBC | Coal tar was used pre-1970 to line iron mains. Coal-tar linings can be discounted in plastic, cement mains or asbestos mains. This material contains compounds, amongst others, called polycyclic aromatic hydrocarbons, some of which are known to be carcinogenic above certain concentrations (consult WHO guidelines). Furthermore, coal tar lining can cause various unpleasant aesthetic issues, including petrochemical like taste and odours. Positive evidence for the presence of coal-tar linings may be the analytical results for PAH's or reports of taste and odour. Determine whether any records exist of the presence of coal tar lined mains. If there is any positive evidence of the presence of coal-tar linings, the person in control can confirm any existing control measures and any planned long term remediation. In the absence of any positive evidence, score the likelihood as 1.
V9 | Do any third parties have access to hydrants or other points in the distribution system? | TBC - No risk | TBC | Third parties (contractors, builders, tenant farmers etc.) should only have access to hydrants via a procedure of authorised permission to operate them. This should only be granted where risk to disturbing deposits has been assessed as low. Where no such system is in place, an appropriate procedure must be implemented which should include control of their use.
V10 | Is there potential contamination of plastic pipes through designated contaminated land, oil from generators/household fuel tanks/fuel stores or solvent spillage? | TBC - No risk | TBC | This relates to not only the presence of these types of pipes, but also the possibility that they could be exposed to contamination and migration of the volatiles through the plastic pipes into the water.
V11 | Are there any pipes exposed and at risk of damage by any means e.g. vermin, vehicle, UV/sunlight damage, overheating or freezing? | TBC - No risk | TBC | Pipes that are laid overground or in shallow trenches may be at risk to damage by gnawing rodents, or accidental damage by other wildlife or livestock or any other means, including those caused by motorised vehicles or machinery. Consider this risk in terms of the pipe material, their position, location, exposure to vermin and other animals, use of surroundings. Freezing or overheating may also occur - regular temperature checks should be undertaken (particularly during extremes of weather, and if overheating regular flushing of the water may help reduce the risk of algal growth, or lagging may help protect from freezing.
V12 | If there are valves in the network which are normally closed, are there measures in place to control when and how they are operated? | TBC - No risk | TBC | Closed valves require periodic operation to prevent them seizing. However, deposits do collect behind them over time and can cause discolouration and turbidity. Therefore such operations must be controlled by an approval procedure, to ensure valve operations are first risk accessed and only carried out by competent persons following an appropriate procedure.
V13 | Are there sections of pipework containing stagnant water? | TBC - No risk | TBC | Characterised by either sections of mains of a relatively large diameter in relation to the demand off it e.g. a 3" main with a trough at the end which is only occasionally used is likely to contain stagnant water; or legs of main with no connections off it therefore no turnover of water or where a low discharge point (i.e. single standpipe). 'Dead legs' of main may be present (no connections off it) which are valved out of the distribution system, which pose a hazard if there are insufficient measures to prevent the valve being operated.
V14 | Where there is copper pipework present, is it corroding? | TBC - No risk | TBC | Where copper pipes are used in the distribution system, these problems can be determined through on-site tests, or may manifest in taste complaints (metallic) or discolouration (blue/green) or laboratory tests.
V15 | Is there the potential for backflow from commercial premises, domestic premises, unauthorised connections, standpipes or unregulated supplies? | TBC - No risk | TBC | If the premises are within the private supply check whether backflow protection is in place. If the supply is a PDS the appropriate Water Company can confirm whether any existing backflow deficiencies have been identifed upstream of the supply to the PDS. All PWS should follow this best practice with back flow devices being installed.
V16 | Are lead pipes present in the supply? | TBC - No risk | TBC | Lead pipes are usually only found in distribution systems laid before the 1970s. Unpainted lead pipes appear dull grey. They are also soft and if they are gently scraped you will see the shiny, silver-coloured metal beneath. Dissolution of lead into the water supply occurs at a higher rate where the pH of the water is lower (more acidic). If found short term measures include advising the consumers to run the tap before use, especially when the water has been standing in the pipes for longer periods of time (e.g. overnight), longer term measures include replacing the lead pipes. If parts of the distribution system are metallic, potentially laid pre-1970 but the person in control is now aware of their material, a first draw sample for lead may be appropriate to confirm.
V17 | Do all junctions in the supply network, particularly animal watering systems and standpipes, have backflow protection? | TBC - No risk | TBC | If there are provisions made to provide water to animal watering troughs or other connections where back-siphonage may occur, e.g. from a hosepipe permanently connected, there is potential for the contents of the trough or container to be back-siphoned into the distribution pipe and for the contents of the trough or container to enter the supply. The contents of a cattle watering trough or a barrel into which the end of a hose is submerged presents a hazard if it enters the supply system. It is essential that where connections are made on the system prior to the first taps to be used for domestic (potable) consumption appropriate back-siphonage prevention devices are fitted.
V18 | Are there any known or potential cross-connections (between different sources, greywater systems, sewage pipes or other waste pipes)? | TBC - No risk | TBC | There should be a clear site plan or schematic with the location (and direction of flow) of the drinking water, greywater or sewage pipes. There should be clear labelling and pipe specification for the different systems - full details in BS 8515 and WRAS guidance Note 9 - 02 -05. Main water connections to any private water supply must be protected from cross-connection and backflow protection is required on the mains supply. Contact the local water company if this is absent or there are any possible contraventions of the Water Fittings Regulations.
V19 | Have there been complaints or reports of water quality problems (e.g. taste, odours or reports of any aquatic animals (freshwater shrimp, louse or worms)? | TBC - No risk | TBC | Ask the operator if there have been any complaints about the water being supplied or have known taste, odour or aquatic animal issues. In England and Wales 50% of drinking water is derived from surface water, which contains small plants (algae) and animals. When surface water is treated the majority of these plants and animals are removed. However some animals and algae can pass through water filters and enter the distribution system. During periods of low flow or stagnation in particular colonies of these animals can develop and therefore be present in the water drawn from the tap. Taste and odours issues may arise from certain algal products such as geosmin.
V20 | 0 | N/A - No risk |  | No guidance available
V21 | 0 | N/A - No risk |  | No guidance available
V22 | 0 | N/A - No risk |  | No guidance available
Section W - DISTRIBUTION: Storage of treated water in the distribution network (including private distribution systems)
W1 | Are all treated water reservoirs covered appropriately e.g. No risk of ingress and/or constructed of suitable material? | TBC - No risk | TBC | The level of protection for all tanks or similar structures should be equivalent to that recommended for the source itself as the potential for contamination to enter the system via such structures is just as high as for the source itself.
W2 | Are all treated water reservoirs of sufficient structural integrity to prevent ingress of contamination, including covers? | TBC - No risk | TBC | Structural cracks and other defects in the roof and sides of the reservoir/tank provide a route of contamination, notably microbiological, via water ingress/rain. The reservoir/tank should be in a good general state of repair. Inspect its condition, looking for points of ingress and weakness, paying particular attention to the roof condition, and areas of notable deterioration or decay, which pose a future risk should the structure come under stress. Where possible carry out internal inspections to determine any points of ingress or potential points of ingress. Flooding the roof during inspections will highlight areas requiring remediation. Any reports from contracted inspections should be consulted to assist with the assessment.
W3 | Is the integrity of the reservoir suitably robust against damage by weather or animals? | TBC - No risk | TBC | The over all structure of the reservoir should be fit for purpose at all times to ensure any risk to its integrity is not compromised. Consider its position and robustness (including the material it is made of) in terms of its exposure to adverse weather in a worse case scenario and livestock within its vicinity.
W4 | Are there any waste water pipes, or waste water storage tanks adjacent to the tanks/reservoirs? | TBC - No risk | TBC | Waste pipes may allow their contents to leach into the soil if damaged and enter the reservoir/tank where its integrity is compromised. Assess available information for example about previous defects, the age of the pipes and their location to determine the likelihood of the hazard presented. Consider whether the pipe(s) could be relocated to lower depth ( avoiding damage) moved to reduce the contamination risk. All contractor on site should be made aware of the location of waste pipes when working on the site.
W5 | Are there any unprotected or inadequately protected access covers and/or vents? | TBC - No risk | TBC | Access covers and air vents present potential routes of ingress of water and other materials, which pose a risk of microbiological contamination and poor aesthetic quality. Vents should be checked to ensure adequate protective mesh is in place to prevent access of vermin and other wildlife, and ingress of general debris (leaves, insects, soil etc). Entry/access covers should be of a robust material, watertight and in a state of good general repair. There should be seals around the opening to the reservoir/tank that are in a sound state of repair (i.e. not in a state of decay, absent or do not provide an adequate seal against ingress).
W6 | Are any treated water reservoirs adequately protected against solar heat gain, vandalism (deliberate contamination of treated water and unauthorised access)? | TBC - No risk | TBC | Reservoirs should be adequately protected against the risk of intentional damage. Covers and access points must be securely locked when not in use and access to these points controlled. Check that the owner has records of all key owners. The reservoir/tank should be suitably robust in structure in a secure location. All tanks must be insulated against solar heat gain or freezing.
W7 | Is there a stock-proof fence around any inspection chambers? | TBC - No risk | TBC | Inspection chambers must be adequately protected by fences that are of appropriate height, material and robustness.
W8 | Are the reservoirs regularly maintained and cleaned with appropriate records? | TBC - No risk | TBC | Verbal assurance from the owner that a reservoir is regularly cleaned/maintained is not evidence in itself that the action is undertaken or that the frequency is appropriate. Examine any available records, such as log books and/or supporting documentation such as contractual work receipts as evidence and in addition look for physical signs that covers and access points are in regular use for this purpose. Annual cleaning is recommended for a surface water supply and frequency for other sources should be determined as appropriate, based on water quality history and the current risk assessment. Note that this question is not applicable to temporary installations / events.
W9 | Is there a regular turn over of water, such that the capacity of the storage vessel matches demand? | TBC - No risk | TBC | Water which remains standing for any length of time in a holding structure will deteriorate to varying degrees depending on the conditions it is exposed to. The level of the water within the reservoir/tank should therefore rise and fall at intervals throughout each day facilitating the constant input of fresh water to the structure. Ask the owner to what extent the water is used on a daily basis to determine whether the water turnover is adequate.
W10 | 0 | N/A - No risk |  | No guidance available
W11 | 0 | N/A - No risk |  | No guidance available
W12 | 0 | N/A - No risk |  | No guidance available
Section X - Premises supplied (applicable to domestic dwelling or commercial premises)
X1 | Is the drinking water supply to any customer premises (kitchen tap) supplied via a loft tank? Note; there is no need to inspect loft tanks, just ask for evidence. If no, move on to question X4. | TBC - No risk | TBC | Many properties served by a private supply, particularly those on smaller supplies, will have a header tank within the property to provide sufficient water pressure for the household and also to act as a balancing tank to equalise the pressure differences experienced in the system when pumps are operating to bring water into the property. However, if the header tank is not properly constructed and protected then any material that may be present in the roof space, whether that be dust or mice or bat droppings, will have the potential to enter the tank and so contaminate the supply. If the property has a header tank which feeds the main domestic (potable) tap, usually the kitchen cold water tap, and that tank is not properly protected then the risk characterisation score should reflect the situation encountered and a “Yes” response entered, and a likelihood of 5. If the header tank is present and unprotected but does not feed the main domestic (potable) tap then the risk assessment can be moderated. If when asked the owner cannot provide the evidence to show the condition, protection and cleaning regime for the tank it must be assumed these factors are not satisfactory and there is a high likelihood of contamination. If this evidence is subsequently provided the score can be reassessed.
X2 | If yes, do all loft tanks have a robust vermin proof cover? | TBC - No risk | TBC | The lid should be made of suitable material, exclude light and be tightly fitting and secure, so that birds, vermin and dust cannot get into the water.
X3 | If yes, is there evidence the loft tanks are cleaned at least once per year? | TBC - No risk | TBC | Tanks should be inspected once per year and depending on the results, an appropriate cleaning regime put in place. Inspections and cleaning should be recorded. Where no records are currently kept, request the person in control to set them up.
X4 | Is there any lead pipe work within the properties? | TBC - No risk | TBC | High levels of lead in drinking waters are usually caused by the dissolution of lead (plumbosolvency) from lead pipe work, tank linings or use of leaded alloys in water fittings. Traces of lead may also be derived from lead solder and from PVC pipes containing lead-based stabilisers. If the pipe is dull-grey and is easy to scratch leaving shiny marks then it is likely to be lead. The UK drinking water quality regulations specify a standard for lead of 10 μg/l to be met by 2013. For small water supply systems the best approach is the replacement of lead-containing materials with non-leaded alternatives. However treatment methods are available to reduce plumbosolvency. Water that has been standing in lead pipes for long periods, for example overnight, should not be drunk. In these circumstances, the tap should be run for long enough to clear the pipes before taking water for drinking or cooking.
X5 | Is the water at the consumers tap clear, taste and odour-free? | TBC - No risk | TBC | Drinking water should be visually clear and free of exceptional odours at the time of the visit. If on-site turbidity tests are carried out the results should be <4NTU.
X6 | Is there adequate backflow protection for any rainwater harvesting systems in place at any of the properties? | TBC - No risk | TBC | In recent years, rainwater harvesting systems are becoming more prevalent and are often fitted to new build properties by design. There are guidelines about their installation to ensure that there is no risk of contaminating other drinking water supplies to the property which the harvesting system is designed to augment (see BS 8515 - Rainwater harvesting systems Code of Practice ). Where a rainwater harvesting system is installed, the pipe work should be separate to the private supply (no cross-connections), should be clearly labelled, and there should be an air gap (or other suitable backflow protection) where the private drinking supply connects to any chamber which also has a rainwater supply. Where the source to a property is originally public water supplies (i.e. a private distribution system) these requirements are covered by the Water Fittings Regulations 1999, which the local water undertaker has a duty to enforce. Otherwise for a private water supply if there is a rainwater harvesting system installed and the consumer is experiencing taste, odour, discolouration or other aspects of water quality with their drinking water then the Local Authority should ask for records of the system installation to determine that there is no risk of cross contamination.
X7 | 0 | N/A - No risk |  | No guidance available
X8 | 0 | N/A - No risk |  | No guidance available
X9 | 0 | N/A - No risk |  | No guidance available
Section Y - Point of use devices ( i.e individual property treatment systems such as UV systems, filter, membrane, Reverse osmosis (RO) under the sink)
Y1 | Is the treatment system maintained to the manufacturer's instructions (filter changeover, cleaning)? | TBC - No risk | TBC | A point of use (POU) device is a property specific treatment device. The manufacturers of each treatment unit will specify the frequency and type of maintenance required. Ask the owner for evidence that this is being adhered to.
Y2 | Is the design of the individual treatment system appropriate for the nature of the raw water quality? | TBC - No risk | TBC | The water quality at each premises will determine the required point of use treatment dependant on the contaminant that the unit should remove or inactivate. Ask for evidence that the unit(s) is designed for the property.
Y3 | 0 | N/A - No risk |  | No guidance available
Y4 | 0 | N/A - No risk |  | No guidance available
Y5 | 0 | N/A - No risk |  | No guidance available
Section Z - MANAGEMENT & CONTROL: To determine the risk rating for this section, answer questions Z2 to Z27 to inform the answer to Z1.There should only one risk rating for this section in Z1.
Z1 | CONFIDENCE IN MANAGEMENT? To determine the risk rating for this section, answer questions Z2 to Z27 to inform the answer to Z1.There should only one risk rating for this section in Z1. | TBC - No risk | TBC | No guidance available
Z2 | Are records kept of key checks e.g. Equipment maintenance, site inspections, on-site tests, etc | - | 0 | No guidance available
Z3 | Are there written procedures for the operation and maintenance of equipment? | - | 0 | No guidance available
Z4 | Are there procedures for responding to alarms, monitors, on-site tests? | - | 0 | No guidance available
Z5 | Is there a written procedure for installations, pipe repairs and maintenance to protect against microbial contamination? | - | 0 | No guidance available
Z6 | Do operators have adequate (even if informal) general hygiene awareness? | - | 0 | No guidance available
Z7 | Is there a documented procedure for operation of valves including authorisation? | - | 0 | No guidance available
Z8 | Are there any records of reservoir cleaning and maintenance? | - | 0 | No guidance available
Z9 | Are the records checked to ensure the required maintenance and checks have been carried out satisfactorily? | - | 0 | No guidance available
Z10 | Is there a stock control process for any chemicals used to ensure their continuous availability? | - | 0 | No guidance available
Z11 | Is there a stock control process for any key spare parts/equipment? | - | 0 | No guidance available
Z12 | Is there a documented contingency plan in the event of power failure, equipment failure? | - | 0 | No guidance available
Z13 | Is the person nominated to manage the supply trained to run and maintain the supply? | - | 0 | No guidance available
Z14 | Is there a nominated person to run the supply when the above person is unavailable? | - | 0 | No guidance available
Z15 | Is there a documented system to report emergencies to management/owner of supply? | - | 0 | No guidance available
Z16 | Are there calibration schedules in place for key dosing and monitoring equipment? | - | 0 | No guidance available
Z17 | Is there a weekly site inspection to check for changes (e.g. Dead sheep, broken fence)? | - | 0 | No guidance available
Z18 | Are there appropriate procedures for rectifying customer complaints? | - | 0 | No guidance available
Z19 | Are there procedures and records in place to inform the LA of any changes to the risk assessment? | - | 0 | No guidance available
Z20 | If a risk assessment has previously been carried out, is there a plan for delivering the required improvements? | - | 0 | No guidance available
Z21 | Is there a detailed plan of the site including details of source, tanks, distribution pipes, valves (material, age) etc. | - | 0 | No guidance available
Z22 | Is there a documented contingency for the supply running out? | - | 0 | No guidance available
Z23 | Do the treatment chemicals and materials conform to Regulation 5? Have all new installations since 2010 complied with Regulation 5 (or equivalent in Wales) – products and processes | - | 0 | No guidance available
Z24 | Do all materials involved in the distribution system conform to Regulation 5? Have all new installations since 2010 complied with Regulation 5 (or equivalent in Wales) – products and processes? | - | 0 | No guidance available
Z25 | Is there a documented procedure for carrying out mains tappings (making new connections into pipes)? | - | 0 | No guidance available
Z26 | Are persons carrying out this work competent and trained in this procedure?(e.g. approved by a water company or part of the Water Safe Scheme)? | - | 0 | No guidance available
Z27 | Any additional site specific hazard(s) associated with management | - | 0 | No guidance available

## Controls_&_Actions
Private Water Supply Risk Assessment - Action Plan
Local Authority: |  | Supply Reference:
Supply Name & Address: |  | 0
Assessor: | Name & Position | Revision
Scope of Hazards: | Brief descriptions of the issues
Conclusion: | Once all actions have been completed what is the status of the Private Supply
Overall supply risk classification
Highest mitigated rating:
Final rating:
Risk No: | Hazard Description
Action plan 1
Main Risk | #N/A
Associated risks | #N/A | #N/A | #N/A
Description of risk root cause | Enter Description
Current mitigation in place | Overtype or select from dropdown list of standard mitigation measures
Additional mitigation Required | Description of the actions required to mitigate the risks
Verification of actions following completion
Deadline for completion |  | Action Owner | Enter name or initials
Status of Actions |  | Mitigated risk ranking
Action plan 2
Main Risk | #N/A
Associated risks | #N/A | #N/A | #N/A
Description of risk root cause | Enter Description
Current mitigation in place | Overtype or select from dropdown list of standard mitigation measures
Additional mitigation Required | Description of the actions required to mitigate the risks
Verification of actions following completion
Deadline for completion |  | Action Owner | Enter name or initials
Status of Actions |  | Mitigated risk ranking
Action plan 3
Main Risk | #N/A
Associated risks | #N/A | #N/A | #N/A
Description of risk root cause | Enter Description
Current mitigation in place | Overtype or select from dropdown list of standard mitigation measures
Additional mitigation Required | Description of the actions required to mitigate the risks
Verification of actions following completion
Deadline for completion |  | Action Owner | Enter name or initials
Status of Actions |  | Mitigated risk ranking
Action plan 4
Main Risk | #N/A
Associated risks | #N/A | #N/A | #N/A
Description of risk root cause | Enter Description
Current mitigation in place | Overtype or select from dropdown list of standard mitigation measures
Additional mitigation Required | Description of the actions required to mitigate the risks
Verification of actions following completion
Deadline for completion |  | Action Owner | Enter name or initials
Status of Actions |  | Mitigated risk ranking
Action plan 5
Main Risk | #N/A
Associated risks | #N/A | #N/A | #N/A
Description of risk root cause | Enter Description
Current mitigation in place | Overtype or select from dropdown list of standard mitigation measures
Additional mitigation Required | Description of the actions required to mitigate the risks
Verification of actions following completion
Deadline for completion |  | Action Owner | Enter name or initials
Status of Actions |  | Mitigated risk ranking
Action plan 6
Main Risk | #N/A
Associated risks | #N/A | #N/A | #N/A
Description of risk root cause | Enter Description
Current mitigation in place | Overtype or select from dropdown list of standard mitigation measures
Additional mitigation Required | Description of the actions required to mitigate the risks
Verification of actions following completion
Deadline for completion |  | Action Owner | Enter name or initials
Status of Actions |  | Mitigated risk ranking
Action plan 7
Main Risk | #N/A
Associated risks | #N/A | #N/A | #N/A
Description of risk root cause | Enter Description
Current mitigation in place | Overtype or select from dropdown list of standard mitigation measures
Additional mitigation Required | Description of the actions required to mitigate the risks
Verification of actions following completion
Deadline for completion |  | Action Owner | Enter name or initials
Status of Actions |  | Mitigated risk ranking
Action plan 8
Main Risk | #N/A
Associated risks | #N/A | #N/A | #N/A
Description of risk root cause | Enter Description
Current mitigation in place | Overtype or select from dropdown list of standard mitigation measures
Additional mitigation Required | Description of the actions required to mitigate the risks
Verification of actions following completion
Deadline for completion |  | Action Owner | Enter name or initials
Status of Actions |  | Mitigated risk ranking
Action plan 9
Main Risk | #N/A
Associated risks | #N/A | #N/A | #N/A
Description of risk root cause | Enter Description
Current mitigation in place | Overtype or select from dropdown list of standard mitigation measures
Additional mitigation Required | Description of the actions required to mitigate the risks
Verification of actions following completion
Deadline for completion |  | Action Owner | Enter name or initials
Status of Actions |  | Mitigated risk ranking
Action plan 10
Main Risk | #N/A
Associated risks | #N/A | #N/A | #N/A
Description of risk root cause | Enter Description
Current mitigation in place | Overtype or select from dropdown list of standard mitigation measures
Additional mitigation Required | Description of the actions required to mitigate the risks
Verification of actions following completion
Deadline for completion |  | Action Owner | Enter name or initials
Status of Actions |  | Mitigated risk ranking

## Outstanding_actions_summary
Private Water Supply Risk Assessment - Summary
Select all cells; copy and paste into an email and return to DWI.Enquiries@defra.gsi.gov.uk
Local Authority: |  |  | Supply Reference:
Supply Name & Address:
Assessor: Name & Position
Status of supply before mitigation actions are undertaken
Risk rating: |  | 0
0 | Full RA tool | 0
Outstanding actions
Description of risk root cause | Risk categories | Remedial actions required to improve the supply |  | Action Owner | Deadline for completion of actions
Enter Description | Main Risk, Associated risks | Description of the actions required to mitigate the risks |  | Enter name or initials | 0
Enter Description | Main Risk, Associated risks | Description of the actions required to mitigate the risks |  | Enter name or initials | 0
Enter Description | Main Risk, Associated risks | Description of the actions required to mitigate the risks |  | Enter name or initials | 0
Enter Description | Main Risk, Associated risks | Description of the actions required to mitigate the risks |  | Enter name or initials | 0
Enter Description | Main Risk, Associated risks | Description of the actions required to mitigate the risks |  | Enter name or initials | 0
Enter Description | Main Risk, Associated risks | Description of the actions required to mitigate the risks |  | Enter name or initials | 0
Enter Description | Main Risk, Associated risks | Description of the actions required to mitigate the risks |  | Enter name or initials | 0
Enter Description | Main Risk, Associated risks | Description of the actions required to mitigate the risks |  | Enter name or initials | 0
Enter Description | Main Risk, Associated risks | Description of the actions required to mitigate the risks |  | Enter name or initials | 0
Enter Description | Main Risk, Associated risks | Description of the actions required to mitigate the risks |  | Enter name or initials | 0

## Lookup Admin (hidden)
Risk No. | Hazard when: | Severity | Hazard Description | Answer | Guidance | Risk |  |  |  | Local Authorities | Risk Mitigation | Current mitigation
A0 | Yes |  | Have there been any changes since risk assessment last carried out? | TBC | Any changes to the equipment, ownership or management should result is a 'Yes' Please use the severity option to determine if these changes are an improvement or deterioration | TBC | No risk |  |  |  | Description of the actions required to mitigate the risks | Overtype or select from dropdown list of standard mitigation measures
A1 | No | 5 | Is there a site plan and/or schematic showing location of source, chambers, tanks, distribution network including valves, pipes, consumer premises etc.? | TBC | A site plan or schematic can be a simple sketch through to a complex engineering drawing depending on the size of the supply. It need not be to scale or include internal domestic plumbing arrangements, but should represent the main components of the supply system. It is essential to understand the layout of the water supply system in order to understand the flow of water from source to tap, and how it is managed and monitored, e.g.by valves, meters and other management devices. If no schematic or site plan is present, risk assessment of the site is difficult if not impossible to achieve. If not present the likelihood should be scored as 5, the person in control should be requested to make arrangements to draw up plans showing any valves, meters, hydrants etc as part of the action plan | TBC | No risk |  |  | Adur District Council | Install monitors linked to either alarms or automatic shut off devices to ensure treatment systems are effective. | Monitors installed which are linked to either alarms or automatic shut off devices to ensure treatment systems are effective.
A2 | No | 5 | Are there any procedures and/or written records for the supply (i.e. for checks, monitoring or maintenance, etc.)? | TBC | An absence of written procedures places reliance on specific individuals, who may not always be available to operate the supply system. Procedures provide a reference for operators and ensure a consistent approach. Records of maintenance and monitoring checks provide a management audit trail, which demonstrate how well a supply is being managed and its performing. If these are absent the person in control should be required to implement them. | TBC | No risk |  |  | Allerdale Borough Council | Install additional filters or carbon filter (GAC) to remove discolouration and additional sand or fabric filter to remove physical particulates. | Additional filters or carbon filter (GAC) present designed to remove discolouration. Additional sand or fabric filter to remove physical particulates.
A3 | No | 5 | Are there any manufacturers' instructions for the equipment on the supply? | TBC | The presence of manufacturers' instructions for key equipment (e.g. pumps, treatment processes, dosing systems, monitors) provides an essential reference for operators and provides a record of equipment requirements as designed. Where any instructions are absent, they should be sought as part of the action plan. | TBC | No risk |  |  | Amber Valley Borough Council | Disinfect and/or flush the supply at an appropriate rate and frequency if there is evidence of sediment/biofilm or particulates in the supply system. | Maintenance and service records are being kept and suitable procedures exist for all aspects of the supply and distribution system
A4 | No | 5 | Is there an emergency plan for the provision of an alternative water supply? | TBC | Loss of supplies can occur for a variety of reasons, which are often unforeseen. Contingency measures to provide alternative supplies should be documented as written procedures to ensure that the relevant people can reference what to do under these circumstances.DWI have provided guidance on the provision of alternative supplies, which can be obtained from their website. Persons in control should demonstrate that procedures are in place. | TBC | No risk |  |  | Arun District Council | Produce/complete/update schematic of the layout of all installed treatment systems, shut off devices and filters. | Security arrangements installed to prevent unauthorised access
A5 | No | 5 | Has the owner or operators had appropriate training for the supply? | TBC | Operators should be competent in the operation of the supply system they are managing, and have an understanding of the need to apply sound hygienic practice. A lack of competency and/or hygiene awareness presents a risk of contamination of the supply. The risk assessor must determine what and when training has been undertaken, and whether it is appropriate. For a complex treatment system such as chlorination or chlorine dioxide disinfection a formal training course maybe required, whereas for a UV system informal training form the supplier with written procedures could be appropriate. This can be achieved through dialogue and evidence through certification or other written records. A judgement as to whether deficiencies present a risk must be made and relevant advice provided. | TBC | No risk |  |  | Ashfield District Council | Implement method of logging all service and maintenance of equipment and structures (pipes to tanks etc). | Protection from wildlife and/or livestock contamination
A6 | Yes | 3 | Does the sampling history identify the presence of any hazards? | TBC | Is the supply sampled, excluding regulatory LA sampling, (i.e. operational)? Confirm what parameters the sample is analysed for and what are the results? Determine if this sampling has identified the presence of any particular hazards which should inform the risk assessment. | TBC | No risk | Treatment stages |  | Ashford Borough Council | Install appropriate security arrangements to prevent unauthorised access | Tank cleaning programme
Section B - SOURCE: All catchments | [7 empty] | Filtration (sand/GAC) |  | Aylesbury Vale District Council | Put in place suitable protection from wildlife and/or livestock | Storage of chemicals, fertilisers, pesticides (including the location of sheep dips) or fuel is restricted in the vicinity of the source (450m).
B1 | Yes | 4 | Are there latrines, septic tanks, animal enclosures or cess pits present within 50m of the source? | TBC | If unsewered human or animal sanitation is present within 50m of the source then there is considerable potential for raw human sewage to contaminate the source of the drinking water supply. If the supply is groundwater and in a high vulnerability area (as indicated in the EA aquifer vulnerability maps), the unsewered human or animal sanitation is highly likely to contaminate the source through underground connectivity. Information on geography and aquifers can be found in teh EA's Magic Maps available on the EA website or magic.defra.gov.uk In high vulnerability areas this contamination risk will be present regardless of the condition of the collection chamber or head works. New sources should not be installed within 50m of unsewered human or animal waste in high vulnerability areas. | TBC | No risk | Membrane filtration |  | Babergh District Council | Implement regular tank cleaning programme | Diversion channels, ditches or bunding to divert flow away from the vicinity of the source. Include regular checks and maintenance.
B2 | Yes | 4 | Are there any waste pipes (sewage) adjacent to the source? | TBC | Defects, deterioration and damage to waste pipes may allow their contents to leach into the soil and enter the source where its integrity is compromised. Determine their contents, material, location (on a site plan) and where possible, their robustness (consider its age) to establish the likelihood of the hazard presented. Consider whether the pipe(s) could be relocated to lower depth ( avoiding damage) or moved to reduce the risk posed. All contractors on site should be made aware of the location of waste pipes when working in the area. To find information on groundwater vulnerability type the post code into the EA web page 'What's in your backyard' and look at the aquifer vulnerability map in the ground water section. | TBC | No risk | Desalination or reverse osmosis |  | Barking and Dagenham | Restrict storage of chemicals, fertilisers, pesticides (including the location of sheep dips) or fuel from the vicinity of the source (450m). | Oil or fuel stores are adequately bunded and marked on the site schematic.
B3 | Yes | 5 | Is there a risk of microbial contamination (from slurry spreading, and/or storage of slurry or dung)? | TBC | The hazard arises from the active application of the materials in conjunction with the disruption of the soil itself, e.g. via ploughing or sub-soil injection. The likelihood value will be based on the probable duration and frequency at which such activities are undertaken. In some areas brownfield sites or derelict land will be remediated using sewage-derived sludge or slurry or similar materials. The rate of application will typically be higher and this should be borne in mind when assessing the risk. To find information on groundwater vulnerability type the post code into the EA web page 'What's in your backyard' and look at the aquifer vulnerability map in the ground water section. | TBC | No risk | UV disinfection |  | Barnet | Identify likely risks and carry out any additional monitoring (sampling) required to confirm | Slurry spreading or slurry lagoon is restricted within 50metres from the source following Environmental Regulations enforced by the Environmental Agency.
B4 | Yes | 4 | Is there a risk of pesticides or chemical contamination (e.g. sheep dipping chemicals) | TBC | If storage / disposal sites for pesticides are known to be close to the source under investigation then the risk characterisation should reflect this. In addition, look for any evidence of sheep dipping activity in the area when assessing the site. Pesticides may also be periodically applied to the land - the timing of which and the nature of the pesticide will depend on the crops being grown or the livestock present. | TBC | No risk | Chlorine disinfection |  | Barnsley Metropolitan Borough Council | Install diversion channels, ditches or bunding to divert flow away from the vicinity of the source. Include regular checks and maintenance. | Backflow protection is installed
B5 | Yes | 4 | Are chemical fertilisers used? | TBC | Chemical fertilizers typically contain nitrates and phosphates, which may enter watercourses through run-off or leaching. Levels will vary depending on the rates of application, weather conditions and the longer term history of applications at the site. | TBC | No risk | Untreated |  | Barrow-in-Furness Borough Council | Install additional treatment systems or blend water supply to ensure compliance with the regulatory standard. | Equipment is protected from flooding
B6 | Yes | 4 | Is there history of mining in the catchment (i.e. chemical or metal contamination)? | TBC | If there is evidence of the area adjacent to the source having been used for mining activity at any time in the past, which may pose a contamination threat then this should be recorded on the risk assessment. Such activities may include mineral, ores or other extraction such as coal mining. The likely hazards include sediment/turbidity from the extraction itself or increased run-off times into water courses, or heavy metals depending on the material being mined. | TBC | No risk | Unknown |  | Basildon District Council | Implement a means of logging all servicing and maintenance of equipment and structures (pipes, tanks etc) | Procedures exist around the purchase of approved treatment chemicals, their delivery, handling and use.
B7 | Yes | 4 | Does the local geology suggest the present of - boron, arsenic, lead, fluoride, uranium, nickel, radon or other potentially harmful natural substance in raw water? | TBC | Minerals and substances such as these parameters are naturally occurring and are likely to be known by the water company, Environment Agency or other Local Authorities who have already carried out risk assessments. Because these are naturally occurring they are likely to affect large areas. the EA or neighbouring authorities are the best sources of ifnoramtion regarding the presence of such substances in the ground water. If the local water company has sources in the area they may be able to confirm or rule out the presence of such substances. | TBC | No risk | Other (details) |  | Basingstoke & Deane Borough Council | Ensure oil or fuel stores are adequate i.e. double skinned, bunded and marked on the site schematic. | Auto shutdown systems exist
B8 | Yes | 4 | Is the source likely to be affected by any contaminated land including landfill sites in the catchment? | TBC | The presence of disposal sites may influence the quality of water at the source by allowing the introduction of microbiological or chemical contaminants into the supply, depending on the nature of the materials being disposed. Incineration is also included in this section as the question of both airborne material and disposal sites for ash residues need to be considered when making the overall assessment of the likely impact on the water quality at the source. the likelihood score should reflect the permanent nature (or longevity) of such sites in terms of their potential to continue to release polluting materials for many years after their immediate use has ceased. This question may include designated contaminated land sites or sites that are potentially contaminated, which have not been designated. | TBC | No risk |  |  | Bassetlaw Borough Council | Install appropriate treatment which is validated for the supply. | Contingency plan in place should the normal source be unavailable
B9 | Yes | 4 | Is there a likelihood of insufficiency of supply i.e. over-abstraction of source or during drought conditions | TBC | Insufficiency caused by low levels of stored water may result in for example (not an exhaustive list) increased algal population (due to increased temperature and sunlight), limescale deposits in ground water, sludge, metal concentrations and reduced oxygen levels. The insufficiency of supplies is a hazard in itself, additionally there are hazards associated with the water levels recharging or replenishing such as increased turbidity, nitrates, pesticides, or cryptosporidium from run-off. | TBC | No risk | Action status |  | Bath & North East Somerset District Council | Carry out a site inspection to check for evidence of seepage from broken waste pipes or blocked soakaways i.e. marshy vegetation or ponding. Identify the cause and undertake the appropriate remedial measures ensuring these works comply with Building Regulations and the manufacturers instructions. . | Suitable and validated treatment systems are in use
B10 | No | 5 | Is the source adequately protected against vandalism (deliberate contamination of source and unauthorised access)? | TBC | Adequate protection will be site specific depending on the level of accessibility of the site to the general public. Measures may include fencing, gates and padlocks, etc. | TBC | No risk | Closed |  | Bedford Borough Council | Prior to the installation of a new treatment system, ensure a competent person disinfects/ chlorinate the supply distribution system | Evidence shows that the equipment is operated according to manufacturer's instructions and is validated
B11 | Yes | 5 | Is there a risk of oil spill entering the supply (e.g. generators, household heating oil, farm fuel, generators, road traffic accident or the presence of a redundant tanker etc.)? | TBC | Are there fuel stores (e.g. domestic tanks) or equipment using fuel, stored within 250m of the source? Check their condition (are they in good repair and adequately bunded and the suitability of their filling procedure to determine the likelihood. | TBC | No risk | On Target |  | Bexley | Restrict or relocate slurry spreading or slurry lagoon respectively, 50metres from the source following Environmental Regulations enforced by the Environmental Agency. | Alarms are available for failure of processes
B12 | Yes |  |  | N/A | No guidance available |  | No risk | Pending |  | Birmingham City Council | Ensure backflow protection is installed especially for animal watering systems, industrial users, etc. | Cold weather protection (and other adverse conditions) is installed
B13 | Yes |  |  | N/A | No guidance available |  | No risk | Delayed |  | Blaby District Council | Secure equipment from unauthorised access and use. | Reservoir and storage tank covers are robust and sound seals are in place to prevent ingress
B14 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Blackburn with Darwen Borough Council | Install appropriate drainage and other measures to protect equipment from flooding | Dosing arrangements are in place to minimise the production of Tri Halo Methanes (THMs) and other disinfection by products (DBP's)
Section B - Radioactivity | [9 empty] | Blackpool Borough Council | Ensure that water is pre-treated to meet <1NTU turbidity before disinfection by UV and or Chlorine; by optimising existing processes or installing suitable treatment
B15 | Yes | 5 | Are there any man made sources of tritium in the catchment which could affect the water supply? | TBC | Man-made sources of tritium are uncommon in England and Wales, and would be as a result of contamination events, discharges or spills. Consult local authority records and the Environment Agency (NRW in Wales) for information on known spills or disposal of tritium. | TBC | No risk |  |  | Blaenau Gwent County Borough Council | Create or modify procedures which govern the purchase of approved treatment chemicals, their delivery, handling and use.
B16 | Yes | 5 | Has the Environment Agency any record of historic pollution event(s) in the catchment which contained radioactive substances? | TBC | Consult with the Environment Agency (NRW in Wales) for information on any historic pollution or contamination events. This should include its location, the nature of the contamination, what was the radioactive substance involved, details of any remediation carried out and details of any ongoing monitoring. | TBC | No risk |  |  | Bolsover District Council | Install suitable and validated treatment to disinfect the source water, ensuring adequate mixing, dose and contact time as appropriate.
B17 | No | 5 | Does the local water company have a notice allowing them to cease monitoring for tritium or ID for abstraction points from the same aquifer? | TBC | Contact the supplying water company and request details of the evidence provided to justify this, results of any samples taken and confirm whether or not the company has been granted a waiver to allow them to reduce or cease analysis for radioactivity. These are valid for a 5yr period and should be used to help inform the risk assessment. | TBC | No risk |  |  | Bolton Metropolitan Borough Council | Ensure the treatment system 'fails safe' thus preventing untreated or partially treated (unsafe) water being supplied and consumed (often referred to as auto shutdown)
B18 | Yes | 5 | Is there any monitoring data (EA/Wco/LA) for radioactive substances in this supply or another supply in the same water body indicating levels above the standard/value? | TBC | If any organisation has monitoring results showing a radioactive substance above the permitted value, the supply should be classified as high or very high risk of exceeding the parametric value, pending further investigation and monitoring. | TBC | No risk | Risk Ranking |  | Boston Borough Council | Create or modify contingency plan to ensure consumers receive an alternate supply should the normal source be unavailable for any reason, including flooding, fire, vandalism, and loss of treatment (malfunction, damage or loss of electricity) for example.
B19 | Yes | 4 | Does the ‘Radioactivity in Food and the environment’ report indicate the likely presence of radioactive substances? | TBC | https://www.food.gov.uk/science/research/radiologicalresearch/radiosurv/rife Where it is established that there is a likely presence of radioactive substances, further information relating to this should be obtained from the EA and PHE. | TBC | No risk |  |  | Bournemouth Borough Council | Provide evidence to demonstrate that the treatment validated and suitable for the levels and types of contaminants present in the source water
B20 | No | 5 | If gross alpha or gross beta exceed the limit, does the Indicative Dose (ID)calculation confirm the value is <0.1mSv? | TBC | If a result of gross alpha or gross beta is above the permitted values, further investigation should be carried out and analysis of individual radionuclides undertaken to calculate the ID. Your laboratory should be able to carry out this analysis and calculation. If it is below 0.1mSv no further monitoring of gross alpha or beta is required. | TBC | No risk | L | Low Risk | Bracknell Forest Borough Council | Provide evidence to demonstrate that the equipment is operated according to manufacturer's instructions and is validated
B21 | Yes |  |  | N/A | No guidance available |  | No risk | M | Medium Risk | Bradford Metropolitan District Council | Create or modify procedures which govern the servicing and maintenance of equipment and associated monitors including records to demonstrate maintenance history
B22 | Yes |  |  | N/A | No guidance available |  | No risk | H | High Risk | Braintree District Council | Create or modify procedures which govern the setting of alarms and response to them to ensure wholesome drinking water is supplied to consumers at all times.
B23 | Yes |  |  | N/A | No guidance available |  | No risk | VH | Very High Risk | Breckland District Council | Ensure treatment is protected from cold weather and other adverse conditions. Make procedures for contingency drinking water supplies should access to the site be lost
Section C - SOURCE: Catchment of Surface Water Supply (including springs) | [9 empty] | Brent | Install and calibrate online monitors and set up associated records to document servicing and maintenance work.
C1 | Yes | 4 | Is there a noticeable change in the appearance of the water from time to time (colour, cloudiness/turbidity)? | TBC | Changes in levels and flows can result in deterioration of raw water quality with associated increases in turbidity and colour due to the suspension of sediment. This will be most prevalent during periods of heavy rainfall, when flooding and rapid runoff of surface water into the source can occur. Associated water treatment must be designed to meet the demands of these "flashy" conditions. | TBC | No risk |  |  | Brentwood Borough Council | Carry out appropriate repairs to pipes, ensuring all fittings are Regulation 5 approved.
C2 | Yes | 3 | Is the source exposed to risks of faecal contamination from wildlife (this will always be yes for all surface water sources, i.e. rivers, lakes and streams)? | TBC | Any evidence of wildlife, mammals (rabbits, deer, etc.), birds (gulls, geese, migratory birds, etc) reptiles ( frogs, newts, etc) at the source could indicate the potential for contamination of the supply either from faecal material or from carcasses falling into the supply. Measures required to mitigate risks from wildlife should take into account the type and extent of risk presented. The occurrence of wildlife might be transient (e.g. from birds overhead) or more regular, where for example, the source is in close proximity to rabbit warrens. | TBC | No risk | Validation of actions |  | Bridgend County Borough Council | Replace pipes, ensuring they are Regulation 5 approved material.
C3 | Yes | 5 | Is there waste-water discharging biological matter into the source? | TBC | Determine (probably during desk top part of assessment) if any sewage treatment works, abattoirs, etc discharge waste upstream of the source intake. | TBC | No risk | Assess records for example photographs, documentation, schematics, maintenance log, service record and certificates |  | Brighton & Hove City Council | Divert pipes/reconfigure the distribution system.
C4 | Yes | 4 | Is there waste-water discharging chemical substances into the source? | TBC | Determine (probably during desk top part of assessment) if any tanneries, paint factories, plating works, etc discharge chemicals upstream of the source intake. | TBC | No risk | Visit site to ensure that the improvements made comply with regulations and mitigate the associated hazard to a suitable level of safety. |  | Bristol City Council | to be lagged or run in conduit appropriate to the hazard (i.e. to prevent deterioration of water quality or contamination by damage or ingress of pipes by any means).
C5 | Yes | 5 | Are there unbunded stores of farm waste or silage in the catchment? | TBC | If there are areas where silage is being stored in polyethylene bags (or equivalent) or other farm-derived wastes (faecal contamination) where there is no bunded storage and there is the potential for spillage entering the source (including via land drains) which are permanent or long-term feature then the likelihood should be scored as 5 . The hazard is high ammonia levels which reduces the effectiveness of chlorine disinfection. Chlorination converts ammonia to chloramines which are less potent disinfectants than chlorine itself and can give rise to taste and odour complaints. Therefore, when designing chlorination systems for ammonia-containing waters, the chlorine capacity must be sufficient to produce a free chlorine residual. | TBC | No risk | Collect samples and assess sample results |  | Broadland District Council | Remove cross connections between pipes carrying different water sources.
C6 | Yes | 3 | Is local forestry activity causing or likely to cause suspended particles in the source water? | TBC | Forestry activities have the potential to increase suspended particles (soil/debris) in the water supplies of the area. The disruption may occur when forests are being planted, thinning activities or harvesting. | TBC | No risk |  |  | Bromley | Put in place robust reservoir/storage tank covers, ensuring sound seals are in place to prevent ingress
C7 | Yes | 4 | Is freshwater aquaculture practised upstream, causing contamination (feed, pesticides etc.)? | TBC | i.e. fish farms. Hazards associated with fish farms are pesticides, particulates from organics feed and waste material, including faecal. | TBC | No risk |  |  | Bromsgrove District Council | Replace/repair the existing structure to ensure that it is suitable robust against risk of damage and/or contamination by any means.
C8 | Yes | 4 | Is there run off from construction/development activities upstream of intake causing contamination (oil spills, silt, cement, bentonites, soakaways, open tanks, surface water inceptors)? | TBC | If there is evidence of the area adjacent to the source having been used for industrial activity which may pose a contamination threat then this should be recorded on the risk assessment. Such activities may include chemical or pharmaceutical production, mineral or other extraction such as coal mining, areas where old fuel tanks may have been located or may still be in place either below or above ground, or industries where solvents would have been in use and may have been disposed of on to the ground, e.g. electroplating, metal working or electronics. | TBC | No risk | Relevance |  | Broxbourne Borough Council | Put in place robust and suitable security measures to protect treated water storage facilities from unauthorised access
C9 | Yes | 4 | Is local quarrying activity causing or likely to cause suspended particles or any chemicals in the source water? | TBC | Local quarrying can increase suspended particles (dust/debris) in the water supplies of the area which can affect disinfection. Consider the level of activity to assess likelihood of hazard. | TBC | No risk | Owner |  | Broxtowe Borough Council | Put in place suitable/adequate drainage arrangements appropriate to the hazard.
C10 | Yes | 4 | Is the source water used for recreational purposes? | TBC | Recreational water can become contaminated especially if there are boating activities, as boats can discharge oil, lavatory waste or other chemicals into the water. The risk of contamination of a PWS by oil or fuel can be reduced by installation of a boom surrounding the intake point. | TBC | No risk | Consumer |  | Burnley Borough Council | Where there are latrines, septic tanks, waste pipes, animal enclosures or cess pits are present in the vicinity of the distribution system, put in place/upgrade appropriate barrier methods to prevent contamination of treated water via ingress/leaching
C11 | Yes | 3 | Is the source water subject to seasonal algal blooms including toxin producing algae (cyanobacteria)? | TBC | The main hazard associated with algae is filter blocking however some species of blue green algae produce toxins. This is a seasonal occurrence therefore check with the person in control if they have experienced this at the supply. Assessment of the associated risk to public health is not straight forward. Such assessment should therefore take account of specialist advice such as "Blue -green algae (Cyanobacteria) in Inland Waters: Assessment and control of risks to public health. | TBC | No risk | Site Location |  | Bury Metropolitan Borough Council | Replace plastic pipes with barrier pipe to prevent migration of solvents/ fuel/oil.
C12 | No | 5 | Is the spring chamber designed and constructed to exclude surface water or spillages of contaminated material causing microbial or other contamination (through the cover or the lining) and is it in a satisfactory state of repair? | TBC | If the chamber is not in a satisfactory state of repair, the lining is not watertight (i.e. where there is deterioration of the cement lining, brick, stone or concrete rings by roots or by other damage) or does not have a watertight cover, then there is a risk of ingress into the spring chamber causing potentially contaminated surface water to enter the supply. If there is evidence that the chamber is not watertight then the likelihood score should reflect the almost certain nature of the hazard | TBC | No risk | Controller |  | Caerphilly County Borough Council | Provide robust documents/records to demonstrate that the method(s) of treatment is/are appropriate to the hazard.
C13 | No | 5 | Does the spring chamber extend at least 150mm above the level of the floor with an apron sloping away from a secure cover? | TBC | If the spring chamber does not extend above the level of the floor then there is an increased risk of the top of the spring chamber either being inundated with water, introducing contamination into the chamber . A secure lockable cover is required to prevent malicious (or just curious) persons gaining access to the supply. If there is no apron sloping away from the spring chamber cover, water can pond around the cover and ingress is likely. If there is evidence of this then the likelihood score is almost certain | TBC | No risk | Other |  | Calderdale Metropolitan Borough Council | Improve dosing arrangements to minimise the production of THMs/ disinfection by- products.
C14 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Cambridge City Council | Put in place/update procedures and records for the controlled and effective management of the distribution network management, such as valve operations, flushing, tap-ins, pipe maintenance and repair.
C15 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Camden | Put in place/update record keeping of water quality monitoring (e.g. chlorine residual measurements, sampling).
C16 | Yes |  |  | N/A | No guidance available |  | No risk | Purpose |  | Cannock Chase District Council | Put in place/update appropriate backflow protection measures to prevent actual or potential contamination of the public supply
Section D - SOURCE: Catchment of Ground Water Supply | [7 empty] | Commercial |  | Canterbury City Council | Put in place/update procedures and records of treated water storage facility cleaning and maintenance
D1 | No | 4 | Where there are abandoned wells or observation boreholes are they adequately capped, fenced and protected? | TBC | If there are unused supplies or wells associated with the supply under investigation then the potential for material to be introduced directly into the source water exists. For example, if an older, out of use well is located adjacent to the currently operational well, any contamination of the out of use well or borehole can affect the water source. To find information on groundwater vulnerability type the post code into the EA web page www.whatsinmybackyard and look at the aquifer vulnerability map in the ground water section. http://publications.environment-agency.gov.uk/PDF/SCHO1000BFHB-B-E.pdf | TBC | No risk | Domestic |  | Cardiff Council | Replace/upgrade treated water storage facility to ensure that its capacity is replenished with fresh water regularly throughout each day (i.e. so that its size is proportionate to usage).
D2 | No | 5 | Are livestock excluded from the vicinity of the headworks (e.g. by fencing) to minimise the risk of microbial contamination? | TBC | Look for any evidence of domestic livestock production being present either directly (by the presence of animals in the vicinity of the supply) or indirectly (through presence of broken ground around the supply or the presence of animal droppings around the supply). http://publications.environment-agency.gov.uk/PDF/SCHO1000BFHB-B-E.pdf. Risks can be increased where the source is in a high vulnerability area ( see B1 Guidance). | TBC | No risk | Single Domestic Dwelling |  | Carlisle City Council | Install a vermin-proof cover not liable to corrosion
D3 | Yes | 4 | Is there evidence of standing water/ponding within 50m of the headworks? | TBC | look for evidence of standing water around the source, or evidence standing water has been present (marshy ground). This indicates the soil around the source is more likely to be saturated and therefore any flow of surface water into the source will be faster. http://publications.environment-agency.gov.uk/PDF/SCHO1000BFHB-B-E.pdf. Risks can be increased where the source is in a high vulnerability area ( see B1 Guidance). | TBC | No risk | Other |  | Carmarthenshire County Council | Clean loft tanks - one off or implement a regular programme (update maintenance records)
D4 | No | 4 | Is the borehole or well appropriately lined with casing and grouted to prevent ingress of shallow subsurface and/or surface water? | TBC | Surface water or subsurface flows can contaminate the borehole/well where there is inappropriate or absent grouting or lining material. This can be protected against through the use of appropriately engineered borehole arrangements. If suitable arrangements are absent from the site then the permanent nature of the deficiency results in a likelihood score of almost certain (value 5). http://publications.environment-agency.gov.uk/PDF/SCHO1000BFHB-B-E.pdf | TBC | No risk |  |  | Castle Point Borough Council | Replace lead pipe-work
D5 | No | 5 | If a chamber is present does it have barrier(s) to prevent ingress of surface water through the walls/floor (grouting/diversion ditch/walls etc.)? | TBC | The borehole needs to be protected from the ingress of surface flows (such as flooding). This can be accomplished in a variety of ways such as having a ditch surrounding the borehole (https://www.gov.uk/government/collections/groundwater-protection) with an impermeable lining and a suitable discharge downslope from the borehole conveying surface water away from the immediate vicinity of the borehole. It should be borne in mind that surface flows, while including flooding, are not restricted to flooding. In certain ground conditions the impermeable nature of the soil during periods of dry weather will produce a surface akin to concrete which will result in rainfall, e.g. a heavy summer downpour, running over the surface rather than percolating into the soil. Such conditions need to be protected against by use of appropriately engineered borehole arrangements. | TBC | No risk |  |  | Central Bedfordshire Council | Replace internal pipework if corroding and causing discolouration
D6 | No | 5 | If a chamber is present does it have a cover that is non-degradable material that would prevent ingress of rainwater, vermin and is lockable (if not inside a locked building)? | TBC | A properly constructed and well-fitting cover is essential to maintaining the integrity of the source. In addition boreholes require a properly constructed and maintained chamber around the headworks with an inspection cover. The borehole/well casing should extend at least 150mm above the level of the floor and there should be a concrete apron, sloping away from the top of the borehole to ensure that any ingress to the housing will always run away from the top of the borehole. Covers should be of a suitable non degradable material, watertight to prevent ingress of rainwater, vermin-proof to prevent animals from entering the well (i.e. with no holes through which small mammals can enter), and lockable to prevent malicious (or curious) persons gaining access to the supply. Points of cable/wiring entry should have water tight seals. If ventilation is present ensure that it is also vermin-proof with appropriate wire mesh in place. http://publications.environment-agency.gov.uk/PDF/SCHO1000BFHB-B-E.pdf | TBC | No risk | Private supply types |  | Ceredigion County Council | Install back-flow protection on washing machines/dishwashers if water tastes of TCP
D7 | No | 4 | Are the headworks completely sealed so that no surface water, spillages or vermin/insects can enter? | TBC | If the headworks are in an unsatisfactory state-of-repair then there is an increased risk of vermin entering or of surface flows inundating the structure. If there is evidence that the headworks are in an unsatisfactory state-of-repair then the likelihood score will be almost certain (value = 5). http://publications.environment-agency.gov.uk/PDF/SCHO1000BFHB-B-E.pdf | TBC | No risk |  |  | Charnwood Borough Council | Install adequate backflow protection between rainwater harvesting system and the drinking water supply (usually an air gap physically separating the systems)
D8 | Yes | 5 | Are there land drains which channel water into the source? | TBC | Drainage systems, ditches, gulleys, channels, etc. can provide routes of ingress into water sources posing a risk of both microbiological and chemical contamination from surface water run-off. The likelihood score should take into account the probable time and extent to which the land is being grazed or subjected to agricultural applications. Mitigation might include diversion of the drainage arrangements or installation of appropriate treatment. Risks can be increased where the source is in a high vulnerability area ( see B1 Guidance). | TBC | No risk | Regulation 8 - Private Distribution Systems |  | Chelmsford Borough Council | Ensure storage tank is of appropriate size and configuration to ensure adequate turnover of water.
D9 | No | 5 | Are there historic results from the supply confirming the radon levels are below 100Bq/l? | TBC | Where historic sample results for the supply are available, these should be a minimum of one year of monitoring data with seasonal variation. These should be used to support the risk assessment. If these indicate a low hazard ratings of source, <100Bq/l, analysis for radon is not required. The local authority can also request information on radon sample results and any waivers currently in place from the local public water supplier to inform this decision. Further information may be found in DWI guidance: http://www.dwi.gov.uk/stakeholders/guidance-and-codes-of-practice/pws-radon-QA.pdf | TBC | No risk | Regulation 9 - Large supplies (10m3/day or more) and those used as part of a commercial or public activity |  | Cheltenham Borough Council | Upgrade point of use treatment device to address raw water quality
D10 | No | 5 | Does the local water company have a waiver for radon for abstraction points in the same aquifer? | TBC | Water companies are obliged to undertake monitoring for radioactive substances in moderate and high hazard sources according to the AEA Ricardo report. Where the results confirmed that the levels were unlikely to exceed 100Bq/l, they were encouraged to apply for notices exempting them from further radon monitoring. Ask the local water company for information relating to radon waivers for sources in the same aquifer if present, and request sample results for this. If sample results have been obtained from a similar aquifer over a year period and are below 100Bq/l, this should inform your risk assessment as to whether monitoring of the private source is required. Further information may be found in DWI guidance: http://www.dwi.gov.uk/stakeholders/guidance-and-codes-of-practice/pws-radon-QA.pdf | TBC | No risk | Regulation 10 (England) – Small or shared (>1 property) supplies, up to 10m3 day |  | Cherwell District Council | Put in place a maintenance regime for the point of use device to include filter or lamp changing, cleaning etc.
D11 | No | 4 | Do radon-in-air measurements confirm the levels are below 200Bq/m3 (where there is no existing radon treatment)? | TBC | Where radon levels in air are below 200Bq/m3, there is no requirement to undertake analysis for radon in water. Where radon levels in air exceed 200 Bq/m3 , installation of treatment may be required. Consideration should be given to any health issues experienced by residents living in the property when making a decision using information provided in PHE guidance on radon in homes: http://www.ukradon.org/ | TBC | No risk | Regulation 10 (England) - A supply to a single dwelling not provided as part of a commercial or public activity |  | Cheshire East Council | Replace/upgrade the UV unit
D12 | Yes | 4 | Does the PHE report or AEA Ricardo report identify the site as moderate or high hazards rating? | TBC | Information provided in these reports identify where a source is considered to be a moderate or high hazard rating for naturally occurring radon. If there is no treatment in place for radon, the local authority should consider undertaking radon in air sampling as part of the investigation. However, where there is treatment in place and the site is still considered to be moderate or high risk, radon in water analysis should be undertaken. Identify what control measures are already in place for dealing with radon. Identify what/where the source of radon is from and undertake analysis for the relevant radionuclides associated with this source. Information on this can be found in the EA Radionulides handbook: https://www.gov.uk/government/uploads/system/uploads/attachment_data/file/291128/sp3-101-sp1b-e-e.pdf Also, refer to PHE for further guidance. | TBC | No risk | Regulation 10 (Wales) – A supply to a single untenanted dwellings only not used as part of a commercial or public activity. |  | Cheshire West & Chester Council
D13 | Yes | 5 | Do sample results indicate radon levels are greater than 1000Bq/l? | TBC | The Euratom and Private Water Supply Regulations require that remedial action is taken if 1000Bq/l is exceeded. Where sample results indicate radon levels >1000Bq/l, a Regulation 18 notice should be issued and identification of any treatment available and in use. If not, treatment will be required. PHE should be consulted to determine if it is a risk to health or not (i.e. if a Reg 18 or section 80 notice is required). Contact PHE for further guidance and information on remedial works to reduce radon:- https://www.gov.uk/government/publications/uk-recovery-handbooks-for-radiation-incidents-2015 and http://dwi.defra.gov.uk/private-water-supply/RHmenu/Updated%20Manual%20on%20Treatment%20for%20Small%20Supplies.pdf | TBC | No risk | Regulation 11 (Wales) - Shared supplies to >1 properties up to 10m3 day and those to single tenanted dwellings. |  | Chesterfield Borough Council
D14 | Yes | 5 | Is the source exposed to risks of faecal contamination from wildlife | TBC | Any evidence of wildlife, mammals (rabbits, deer, etc.), birds (gulls, geese, migratory birds, etc) reptiles ( frogs, newts, etc) at the source could indicate the potential for contamination of the supply either from faecal material or from carcasses falling into the supply. Measures required to mitigate risks from wildlife should take into account the type and extent of risk presented. The occurrence of wildlife might be transient (e.g. from birds overhead) or more regular, where for example, the source is in close proximity to rabbit warrens. | TBC | No risk |  |  | Chichester District Council
D15 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Chiltern District Council
D16 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Chorley Borough Council
D17 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Christchurch Borough Council
Section E - SOURCE: Mains water supplied by means of pipes (Regulation 8 supplies) | [9 empty] | City of London
E1 | Yes | 4 | Is there evidence the supply main is coal tar lined? | TBC | Coal tar was used pre-1970 to line iron mains to protect them from corrosion. This material contains compounds, amongst others, called polycyclic aromatic hydrocarbons, some of which are known to be carcinogenic above certain concentrations (consult WHO guidelines). Furthermore, coal tar lining can cause various unpleasant aesthetic issues, including petrochemical like taste and odours. Positive evidence for the presence of coal-tar linings may be the analytical results for PAH's or reports of taste and odour. Checks can be made via water company websites for failures of these parameters. In addition, checks can be made with the water company to determine any recorded coal tar lined mains, and whether the local area was relined as part of its renovation programme. If there is any positive evidence of the presence of coal-tar linings, the water company can confirm any existing control measures and any planned long term remediation. In the absence of any positive evidence, score the likelihood as 1. | TBC | No risk |  |  | Colchester Borough Council
E2 | Yes | 3 | Are there sediments in the main? | TBC | Sediment in mains may be present as particles of iron, manganese and aluminium caused by the corrosion of cast iron mains or when these have not been removed effectively by treatment. When sediments are mobilised they cause transient aesthetic issues. Failures of iron, manganese and turbidity can be checked through water company websites. In addition, checks can be made with the water company to determine the number of consumers who reported discolouration in the supply area within the last 12 months. | TBC | No risk |  |  | Conwy County Borough Council
E3 | No | 3 | Is the section of main upstream of the point of supply subject to good turnover of water (e.g. are there connections to properties nearby which would ensure the water is refreshed in the main constantly)? | TBC | Water that remains standing due to a lack of demand or throughput of water for any reason will stagnate over time causing the water quality to deteriorate. Surges of demand downstream, and notably where there is a sudden downstream drop in pressure will pull this poor water quality into supply leading to aesthetic issues. Consult with the water company to determine if there is evidence of poor turnover through taste and odour breaches or complaints, discolouration issues or detection of microbiological indicators such as coliform failures or elevated colony counts. In the absence of positive evidence of poor turnover, score the likelihood as 1. | TBC | No risk |  |  | Copeland Borough Council
E4 | No | 3 | If the area feeding the supply has had water quality related complaints in the last 12 months, have the causes been mitigated? | TBC | Checks can be made with the relevant water company to determine if there have been higher than average numbers of complaints in the local area in the last 12 months, and if so whether the cause has been identified and remediated. | TBC | No risk |  |  | Corby Borough Council
E5 | Yes | 5 | Have any chemical parameters exceeded the standard in the previous 12 months in the mains supply? | TBC | Water companies are duty bound to comply with the Water Supply (Water Quality) Regulations 2000 (as amended) and supply water that is wholesome, as defined by those regulations. The Water Company is also duty bound to monitor its supplies to demonstrate to the DWI that it complies with the regulations. The information/data provided by this monitoring is made available to the general public, usually via company websites. This should be consulted to provide assurance that the supply has been consistently wholesome for 12 months prior to the risk assessment. The company may also have notices, undertakings or authorised departures on this supply specifying improvement works to achieve a wholesome supply. Where these are in place, confirm what remedial action is required and when it will be delivered. | TBC | No risk |  |  | Cornwall Council
E6 | Yes | 4 | Are there backflow protection deficiencies at any upstream industrial or commercial premises? | TBC | Chemical or microbiological contamination from upstream industrial and/or certain types of commercial activities such as printers, manufacturing businesses, dry cleaners, abattoirs, etc. can occur where there is a lack of, or inadequate, protection against the back-siphonage of contaminated water where compliance with the Water Supply (Fittings) Regulations has not been met. Check with the water company whether any current backflow protection deficiencies have been identified at any upstream commercial/industrial premises through their water fittings inspections programme. | TBC | No risk |  |  | Cotswold District Council
E7 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Coventry City Council
E8 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Craven District Council
E9 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Crawley Borough Council
Section F - This section has been left blank intentionally. | [9 empty] | Croydon
F1 | No | 5 | Is the supplier/contractor competent to undertake the requirements of BS 8551 - Provision and management of temporary supplies and distribution networks.? | N/A | BS 8551 is the code of practice for the provision and management of temporary supplies and distribution networks. Adherence to this code of practice provides assurance that required standards to prevent any contamination are met. Written confirmation that the supplier is following this code of practice must be demonstrated to reduce the risk of contamination. |  | No risk |  |  | Dacorum Borough Council
F2 | No | 5 | Is the tanker suitable in accordance with BS 8551? | N/A | The tanker should be suitable for use to contain and deliver a wholesome supply. It should be robust, vandal proof, and in a general state of good repair. The tanker should comply with Regulation 5 of the Private water Supplies Regulations (e.g. WRAS approved). The use of the tanker for supplying drinking water should be carried out in accordance with the specifications of BS 8551, which includes requirements for cleaning, disinfection, filling of tanker or water bowser, and sampling. |  | No risk |  |  | Dandridge District Council
F3 | No | 5 | Has the tanker been used exclusively for water (i.e. not previously used for milk)? | N/A | Any storage facility used previously for any other liquid presents a potential risk to human health. Containers which have previously contained milk are difficult to clean - steam cleaning of metal containers can result in organic matter and bacteria becoming baked on to the internal surface, and later breaking down into the water. If they have been used for anything other than water they must provide evidence that the tanker has been adequately cleaned prior to disinfection. Those previously used for milk or glucose should be avoided. |  | No risk |  |  | Darlington Borough Council
F4 | No | 5 | Has the tanker been cleaned and disinfected as specified in BS 8551? | N/A | BS 8551 is the code of practice for the provision and management of temporary supplies and distribution networks. Adherence to this code of practice provides assurance that required standards to prevent any contamination are met. Written records to show that the relevant steps have been followed must be provided. |  | No risk |  |  | Dartford Borough Council
F5 | No | 5 | Are records available to demonstrate activities have been undertaken in accordance with BS 8551? | N/A | BS 8551 is the code of practice for the provision and management of temporary supplies and distribution networks. Adherence to this code of practice provides assurance that required standards to prevent any contamination are met. The water service provider must provide evidence that the source water is wholesome in accordance with BS8551, stating the origin and description of the source water. |  | No risk |  |  | Daventry District Council
F6 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Denbighshire County Council
F7 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Derby City Council
F8 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Derbyshire Dales District Council
Section G - This section has been left blank intentionally. | [9 empty] | Doncaster Metropolitan Borough Council
G1 | No | 5 | Does the supplier/contractor operate in accordance with BS 8551? | N/A | BS 8551 is the code of practice for the provision and management of temporary supplies and distribution networks. Adherence to this code of practice provides assurance that required standards to prevent any contamination are met. Written evidence that the supplier is following this code of practice must be provided to confirm any contamination risks are reduced. |  | No risk |  |  | Dover District Council
G2 | No | 5 | Is the temporary water storage facility suitable in accordance with BS 8551? | N/A | Storage facilities can comprise tankers, static tanks, bowsers, pillow tanks, etc. and the code of practice specifies which are appropriate and how they should be deployed. Documentation should be provided to confirm this. |  | No risk |  |  | Dudley Metropolitan Borough Council
G3 | No | 5 | Has the temporary water storage facility previously been used exclusively for water (i.e. not previously used for milk)? | N/A | Any storage facility used previously for any other liquid presents a potential risk to human health. Containers which have previously contained milk are difficult to clean - steam cleaning of metal containers can result in organic matter and bacteria becoming baked on to the internal surface, and later breaking down into the water. If they have been used for anything other than water they must provide evidence that the tanker has been adequately cleaned prior to disinfection. Those previously used for milk or glucose should be avoided. |  | No risk |  |  | Durham County Council
G4 | No | 5 | Has the temporary water storage facility been cleaned and disinfected as specified in BS 8551? | N/A | BS 8551 is the code of practice for the provision and management of temporary supplies and distribution networks. Adherence to this code of practice provides assurance that required standards to prevent any contamination are met. Request evidence that the required steps have been followed to confirm this. |  | No risk |  |  | Ealing
G5 | No | 5 | Does the source water originate from a wholesome supply i.e. a wholesome mains water/borehole/well/spring? | N/A | The water service provider must confirm the requirements of BS8551 have been met, in respect of the wholesomeness of the source water. Details of the source and evidence of its quality should be provided. |  | No risk |  |  | East Cambridgeshire District Council
G6 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | East Devon District Council
G7 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | East Dorset District Council
G8 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | East Hampshire District Council
Section H - This section has been left blank intentionally. | [9 empty] | East Hertfordshire Council
H1 | No | 5 | Are the hoses used for filling clean, and suitable according to BS8551? | N/A | BS 8551 is the code of practice for the provision and management of temporary supplies and distribution networks. Adherence to this code of practice provides assurance that required standards to prevent any contamination are met. Hoses that are not suitable pose a risk of contamination. Request evidence that the required steps have been followed to confirm this. |  | No risk |  |  | East Lindsey District Council
H2 | No | 5 | Are the hoses used for filling stored off the ground on a reel and capped off? | N/A | Hoses that are not appropriately stored and/or are stored uncapped present a risk of contamination from the surrounding environment by various means including those posed by vermin or unclean ground conditions. They must be stored on a reel that is placed on a robust platform ensuring that it is clear of the ground. Pipe ends must be suitably and securely capped. |  | No risk |  |  | East Northamptonshire District Council
H3 | No | 5 | Are the outlets of the tank or tanker protected (bagged) and sealed? | N/A | Protecting the inlets and outlets of the tanks using, for example, plastic bags helps reduce the risk of contamination while in transit or during deployment. |  | No risk |  |  | East Riding of Yorkshire Council
H4 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | East Staffordshire Borough Council
H5 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | East Suffolk Council
Section I - SOURCE: Rainwater harvesting | [9 empty] | Eastbourne Borough Council
I1 | No | 5 | Is there any protection against faecal or chemical contamination e.g. from wildlife or industrial emissions? | TBC | Rainwater contains traces of atmospheric and environmental pollutants and will be exposed to animal and bird faecal matter as it runs off the rooves. The extent of the contamination will vary from site to site but it is surfaces that offer the highest risk in terms of water contamination. e.g. if there are heavy industrial processes nearby, this can be the source of atmospheric pollutants. Therefore all rainwater harvesting systems are high risk and need specific protection against chemical and microbiological contaminates. | TBC | No risk |  |  | Eastleigh Borough Council
I2 | No | 4 | Are there any screens to prevent material entering the collection chamber (e.g. leaves, insects, twigs)? | TBC | Leaves, twigs and organic matter can enter the collection chamber or pipework, causing blockages and, if allowed to deteriorate, the build up of sludge in tanks and pipes. This can provide nutrients for micro-organisms, together with turbid water. Simple particulate filters or screens of a suitable mesh size positioned on guttering and at the intake to the collection chamber can be effective, and regular cleaning of screens is required. | TBC | No risk |  |  | Eden District Council
I3 | Yes | 4 | Are there any trees overhanging the roof? | TBC | Overhanging trees can increase the quantity of leaves, twigs and organic matter filling and blocking any screens or filters. In addition overhanging trees provide habitat for birds, increasing the faecal loading on the roof. Branches overhanging the roof may be trimmed to minimise this hazard. | TBC | No risk |  |  | Elmbridge Borough Council
I4 | Yes | 4 | Is there evidence of lead, tin, copper, asphalt, new galvanised sheeting or wood preservatives on the roof? | TBC | Water collected from rooves will be subject to contamination by lead, tin, copper, asphalt, zinc or hydrocarbons depending on the nature and extent of the roof materials. The likelihood score should be based on the surface area covered by any of these materials. | TBC | No risk |  |  | Enfield
I5 | No | 5 | Is there a bypass mechanism to exclude the first flush of rainwater from the roof? | TBC | A bypass mechanism which excludes the first flush of rainwater from the roof is beneficial because during dry periods the roof surface will accumulate dirt, faecal matter, organics, pollutants, etc, which will be concentrated into the first burst of rainfall which hits the roof and runs off into the rainwater harvesting system. If this first flush of rainwater is discarded the highly contaminated water will not enter the supply. | TBC | No risk |  |  | Epping Forest District Council
I6 | Yes | 5 | Is there adequate backflow protection for any rainwater harvesting systems in place at any of the properties? | TBC | Rainwater harvesting systems as a drinking water source may be augmented or backed up with other drinking water supplies. There are guidelines about their installation to ensure that there is no risk of contaminating any other drinking water supplies to the property (see BS 8515 - Rainwater harvesting systems Code of Practice). Where a rainwater harvesting system is installed, the pipework should be clearly labelled, and there should be an air gap (or other suitable backflow protection) between it and any other water source. Where a property also has a public water supply these requirements are covered by the Water Fittings Regulations 1999, which the local water undertaker has a duty to enforce. | TBC | No risk |  |  | Epsom and Ewell Borough Council
I7 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Erewash Borough Council
I8 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Exeter City Council
I9 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Fareham Borough Council
Section J - SOURCE: Surface Water Intake (excluding springs) | [9 empty] | Fenland District Council
J1 | Yes | 3 | Does the water quality vary at the intake point due to streaming/stratification/algal blooms/increased turbidity? | TBC | Where possible the intake should be located to ensure minimal variation in raw water quality. Where this is not the case the supply may be vulnerable to unexpected changes such as increased turbidity during heavy rainfall which may affect the efficacy of any subsequent treatment. Other factors affecting raw water quality include stratification, algal blooms or streaming. Streaming is where water short-circuits across a body of water; if contaminated any dilution effect will be reduced. | TBC | No risk |  |  | Flintshire County Council
J2 | No | 3 | Are there screens in place at the intake? | TBC | Intakes should generally be protected by screens which remove weeds and debris from the raw water and prevent access by larger fish and vermin. | TBC | No risk |  |  | Forest of Dean District Council
J3 | No | 3 | Where screens are present, is there a mechanism to remove debris? | TBC | A build up of debris on intake screens reduce flow and may cause a deterioration in the quality of the water supply. Screens therefore need to be cleaned by mechanical or manual means. Screens should also be suitably sized and located to provide maximum protection. Ask the site representative (owner/operator) for details of who is responsible for checking the screens and how often. Check any records available. | TBC | No risk |  |  | Fylde Borough Council
J4 | Yes | 3 | Does sediment build up inside the chamber and pipework after the intake point? | TBC | Surface water is very susceptible to sludge/sediment build up due to the exposed nature of the source to the environment. Therefore settlement chambers after the intake points are useful to allow suspended particles to settle out. However the outlet of the chamber should be raised to prevent otherwise settled material access to the rest of the supply system. Check the mechanism to empty the settlement chamber (drained down or periodically suctioned out) and ask how often this is done. Over time the chamber will fill with sediment which can spill over into the water supply (causing turbid water - which will be unacceptable to consumers or may impact on any available treatment such as UV). Like all tanks it should be constructed of materials that will not adversely affect water quality and be designed to prevent unauthorised access or entry of vermin. | TBC | No risk |  |  | Gateshead Metropolitan Borough Council
J5 | No | 5 | Is there adequate protection of the intake point from livestock and wildlife? | TBC | If vulnerable to wildlife and livestock the intake must be adequately protected to prevent disturbance of sediment and deposits, which could enter the supply. | TBC | No risk |  |  | Gedling Borough Council
J6 | Yes | 3 | Does the availability of the water at the intake vary? | TBC | If this occurs, there is also the potential for insufficiency. Changes in levels and flows can result in deterioration of raw water quality causing increases in turbidity and colour due to the suspension of sediment. This will be most prevalent during periods of heavy rainfall, when flooding and rapid runoff of surface water into the source can occur, but this can also be in period of drought. Appropriate water treatment must be in place to meet the demands of these "flashy" conditions. | TBC | No risk |  |  | Gloucester City Council
J7 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Gosport Borough Council
J8 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Gravesham Borough Council
J9 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Great Yarmouth Borough Council
Section K - SOURCE: Water Storage (prior to treatment) | [9 empty] | Greenwich
K1 | No | 3 | Is there a regular turn over of water? | TBC | The size of the tank should be proportional to demand. Water which remains standing for any length of time in a holding structure will deteriorate to varying degrees depending on the conditions it is exposed to. The level of the water within the reservoir/tank should therefore rise and fall at intervals throughout each day facilitating the constant input of fresh water to the structure. As a guide in raw water storage tanks, the water should be turned over (replenished due to use) every 7 days to avoid taste and odour issues and microbial or biofilm growth. Ask the owner to what extent the water is used on a daily basis and whether the capacity matches the demand, i.e. If the tank is too small then there may be a risk of insufficiency or if the tank is too large water may stand for long periods due to low demand. | TBC | No risk |  |  | Guildford Borough Council
K2 | Yes | 4 | Are the storage tanks vulnerable to ingress, flooding or other microbial contamination (e.g. wildlife access)? | TBC | The level of protection for all intermediate tanks or similar structures should be equivalent to that recommended for the source itself as the potential for contamination to enter the system via such intermediate points is just as high as for the source itself. | TBC | No risk |  |  | Gwynedd County Council
K3 | No | 4 | Is there a stock-proof fence around any inspection chambers? | TBC | Inspection chambers must be adequately protected by fences that are of appropriate height, material and robustness | TBC | No risk |  |  | Hackney
K4 | No | 4 | Are the tanks regularly maintained to preserve their structural integrity and cleaned? | TBC | Verbal assurance from the owner that a reservoir is regularly cleaned/maintained is not evidence in itself that the action is undertaken or that the frequency is appropriate. Examine any available records, such as log books and/or supporting documentation such as contractual work receipts as evidence and in addition look for physical signs that covers and access points are in regular use for this purpose. | TBC | No risk |  |  | Halton Borough Council
K5 | No | 4 | Are the storage tanks adequately protected against vandalism? | TBC | Tanks should be adequately protected against the risk of intentional damage. Covers and access points must be securely locked when not in use and access to these points controlled. Check that the owner has records of all key owners. The reservoir/tank should be suitably robust in structure in a secure location. | TBC | No risk |  |  | Hambleton District Council
K6 | No | 4 | Is the cleaning regime for the tank appropriate? | TBC | Sediment and sludge build up is expected, but should be minimised through the design and operation of the tank including maintenance activities. Appropriate cleaning means sufficient cleaning to prevent sediment or sludge build up, before it causes microbiological growth or aesthetic risk. | TBC | No risk |  |  | Hammersmith and Fulham
K7 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Harborough District Council
K8 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Haringey
K9 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Harlow District Council
Section L - TREATMENT PLANT: Plant Design (i.e. excluding point of use devices in dwellings or premises) | [9 empty] | Harrogate Borough Council
L1 | No | 5 | Is there adequate Cryptosporidium treatment in place? | TBC | Found in faecal matter such as from livestock, wildlife and in sewage, Cryptosporidium can affect any surface water sources or vulnerable ground water sources influenced by surface water. A multi-barrier approach is recommended to remove Cryptosporidium from supplies; coagulation, clarification and filtration for example. Chlorination is not effective against Cryptosporidium, however, UV treatment will inactivate it. | TBC | No risk |  |  | Harrow
L2 | No | 5 | Is the treatment plant operating within the design capacity? | TBC | For any treatment process there are operational limits beyond which treatment performance diminishes. The quality of the drinking water being produced may be adversely affected if this occurs. Therefore any process being used beyond its designed capacity or specification requires action to be taken. Refer to any available information provided by the manufacturer on the design specification for the treatment and criteria on which the treatment process was designed. Check whether the 'demand' on the supply has significantly increased since the plant was designed and built e.g. additional commercial premises, large numbers of additional houses. Check the volume of water being treated and the type of treatment process. Flows greater than design capacity will compromise water quality, due to insufficient contact time with UV or overloading of filters for example. | TBC | No risk |  |  | Hart District Council
L3 | Yes | 5 | Is it possible to by-pass any stage of treatment? | TBC | Check for pipe work and/or valves that by-pass any treatment stage. If a UV lamp can be easily switched off (e.g. to save electricity) this is bypassing a treatment stage. | TBC | No risk |  |  | Hartlepool Borough Council
L4 | No | 4 | Where there is a blending facility, is there an appropriate blending strategy? | TBC | Blending can be the mixing of a public water supply with a private supply or between multiple private water sources. This may be carried out to meet water quality standards. Assessment of the blending strategy requires interpretation of sample results and knowledge of seasonal variations e.g. of boron, arsenic, fluoride and nitrates. Check that procedures are in place for the calculation and management of the blending ratio. I.e. are the sources being blended in the correctly quantities to meet the criteria defined in procedures to eliminate exceedances of the standards? Does the strategy take into account seasonal variations? | TBC | No risk |  |  | Hastings Borough Council
L5 | Yes | 4 | Are there frequent flow variations through the treatment plant, which render the treatment process inadequate? | TBC | Variation in flow rates can cause low pressure, insufficient or loss of supply to properties. Flow variations may also compromise water quality by affecting coagulation, clarification, filtration and disinfection treatment processes, particularly when sudden changes occur. Changes to flow rates should therefore be made gradually and should not exceed the design capacity of any individual treatment process. | TBC | No risk |  |  | Havant Borough Council
L6 | Yes | 3 | Are there frequent demand variations, which could cause insufficiency? | TBC | Check whether properties or draw-off points fed by the supply ever run out of water. Treated water storage tanks can be used to help balance fluctuations in demand. Alternatively actions can be taken in the downstream network to reduce demand such as water efficiency measures. | TBC | No risk |  |  | Havering
L7 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Herefordshire
L8 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Hertsmere Borough Council
L9 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | High Peak Borough Council
Section M - TREATMENT PLANT: Filter beds (sand, anthracite, etc) | [9 empty] | Hillingdon
M1 | No | 5 | Is there adequate pre-treatment (e.g. clarification) in place if required? | TBC | Filtration may be preceded by clarification processes dependant on the quality of the source water and corresponding design of the treatment works. Clarification by coagulation is typically installed to remove the majority of colour and turbidity from the raw water. Evidence of the requirement for pre-treatment or of inadequate pre-treatment is an increased frequency of filter blocking or backwashes being required. | TBC | No risk |  |  | Hinckley and Bosworth Borough Council
M2 | No | 5 | Is there adequate process control for filtration (e.g. turbidity monitors)? | TBC | Filter performance may be determined using turbidity monitors - ideally on the outlet of each filter. Where filtered water turbidity is higher than 1.0NTU or where this value is frequently approached then action is needed to improve filter performance and/or any preceding treatment processes. A typical filter cycle will show increased turbidity at the start and end of the cycle (after commissioning and prior to backwashing or refurbishment); these are normal and should be managed operationally. | TBC | No risk |  |  | Horsham District Council
M3 | Yes | 5 | Can the filters overload? | TBC | Check that the filters are managed so they cannot overload; the number of filters should be appropriate to the volume of water being processed. The operator should ensure that the incoming water isevenly distributed across all filters. | TBC | No risk |  |  | Hounslow
M4 | Yes | 5 | Do the filters block? | TBC | Confirm whether the operator checks the filters e.g the surface should appear an even colour, they should be monitored for headloss and turbidity. Determine the regularity of these checks, and of backwashes and media replacement. | TBC | No risk |  |  | Hull City Council
M5 | No | 5 | Is the media depth at a minimum to design specification? | TBC | Confirm with the person responsible for maintenance how they check media depth and ensure minimum depth is maintained as per the manufacturer's specification. | TBC | No risk |  |  | Huntingdonshire District Council
M6 | No | 5 | Is the filter media composition as per design specification? | TBC | Confirm with the person responsible for maintenance whether the media composition is per the manufacturer's specification. | TBC | No risk |  |  | Hyndburn Borough Council
M7 | No | 5 | Is the backwashing regime operated to the design manual (including cycle length, uneven scour, pump failure, loss of filter media) | TBC | Filters are cleaned by the process of backwashing which is typically triggered by filter headloss or increased turbidity of the filtered water. Operators should observe the entire backwash process for each filter for signs of problems such as; uneven bed surface, cracked surface, uneven airscour pattern, presence of vegetation/plants, media loss, effectiveness of wash and wash times. Check with the operator and the documented procedures to determine the criteria for initiating backwashes. Determine whether an appropriate procedure adn records exist that such observations are being made regularly. | TBC | No risk |  |  | Ipswich Borough Council
M8 | No | 5 | Do the filters appear well maintained? | TBC | Check the general structural condition of filters for major issues and confirm the maintenance regime. | TBC | No risk |  |  | Isle of Anglesey County Council
M9 | No | 5 | Does the water run to waste when rapid gravity filters are started up? | TBC | Ask the person responsible for maintenance, if the filters can be run to waste on start up to prevent potentially inadequately filtered water entering the supply. | TBC | No risk |  |  | Isle of Wight Council
M10 | No | 5 | Can the filters be started up gradually (i.e. not immediately run at full capacity)? | TBC | During the early phases of a filter cycle the turbidity of the filtered water will be high. Slowly starting the filters, gradually increasing the flow is a means of minimising the impact of this stage on the quality of the drinking water being produced. | TBC | No risk |  |  | Isles of Scilly
M11 | No | 5 | Where Cryptosporidium is potentially present in the raw water, is a turbidity of less than 1.0 NTU achieved in the filtered water? | TBC | A well operated filter provides a good barrier against Cryptosporidium. Filtered water should have a turbidity well below the 1NTU required prior to disinfection. | TBC | No risk |  |  | Islington
M12 | Yes | 5 | Is the backwash water recycled to head of works? | TBC | Backwash water will contain debris washed out of the filter media during cleaning including microbial contaminants such as algae and Cryptosporidium. Ideally backwash water is run to waste or into tanks for disposal. However, this water may be pumped back to the start of the treatment process. Due to the nature and concentration of the contaminants present, the reuse of backwash water should be appropriately controlled to prevent its reuse under certain conditions (high turbidity). Check with the operator whether such controls are in place. | TBC | No risk |  |  | Kensington and Chelsea
M13 | Yes | 3 | Is algal growth apparent in/on filters? | TBC | Some algal and weed growth on slow sand filters is normal . It is only problematic if the growth becomes excessive. | TBC | No risk |  |  | Kettering Borough Council
M14 | No | 5 | For slow sand filters, is the required ripening period adhered to before putting the water into supply? | TBC | A new biological layer, or Schmutzdecke, will form between 2 days and 2 weeks after the filter is back in operation. This layer is crucial to the effectiveness of the filter, and therefore until it has established, the filtered water should be returned to the start of the treatment process or discarded as it will not have been adequately treated. | TBC | No risk |  |  | King's Lynn and West Norfolk Borough Council
M15 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Kingston upon Thames
M16 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Kirklees Council
Section N - TREATMENT PLANT: Granular Activated Carbon (GAC) filters | [9 empty] | Knowsley MBC
N1 | No | 5 | Has the GAC been installed as per the design specification? | TBC | Granular activated carbon (GAC) is used when removal of organic compounds (such as pesticides) is necessary. GAC is used in a number of ways; a layer can be incorporated into a conventional sand filter (to make a dual media filter); it may replace the sand filter stage or be used after the sand filtration stage. The design of the GAC adsorbers should be based on source water characteristics. | TBC | No risk |  |  | Lambeth
N2 | No | 5 | Is the GAC design appropriate for the nature of the raw water quality? | TBC | GAC is used to remove many types of organic compounds, including the majority of pesticides. However, there are several forms of GAC and the selection of the most suitable form is mostly dependant on its ability to remove the specific organic compounds to be reduced or removed. Check the type and grade and its intended application with the manufacturers product specification. | TBC | No risk |  |  | Lancaster City Council
N3 | No | 4 | Is the media depth and composition appropriate for the nature of the raw water quality? | TBC | Checks should be made to ensure an adequate amount of media is maintained in each filter. This is usually achieved by regularly measuring the filter bed depth which will highlight any loss of media over time. Determine whether this activity being carried out and what do the records show if it is being carried out. If there is evidence that media is being lost then action will be required to prevent further loss either by redesigning the filter and or modifying the backwash process. Ask the operator how they check media composition depth and what triggers media replacement. Limited air scouring is used when backwashing GAC filters to prevent media loss. | TBC | No risk |  |  | Leeds City Council
N4 | No | 4 | Is the plant regularly operated and maintained according to the design specification? | TBC | GAC has an adsorption capacity and its ability to remove organic compounds expires once the surface of the carbon is saturated with organic compounds. At this point, the carbon will either need to be replaced or regenerated. Without this maintenance, the filter is no longer effective as an adsorber - its principal purpose. Check maintenance records and establish if these activities are being carried out according to recommended frequency. | TBC | No risk |  |  | Leicester City Council
N5 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Lewes District Council
N6 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Lewisham
N7 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Lichfield District Council
Section O - TREATMENT PLANT: Ion Exchange (may be used for nitrate, arsenic or manganese removal etc.) | [9 empty] | Lincoln Council
O1 | No | 5 | Is the treatment plant operating within its design capacity? | TBC | For any treatment process there are operational limits beyond which treatment performance diminishes. The quality of the drinking water being produced may be adversely affected if this occurs. Therefore any process being used beyond its designed capacity or specification requires action to be taken. Refer to any available information provided by the manufacturer on the design specification for the treatment and criteria on which the treatment process was designed. Check whether the 'demand' on the supply has significantly increased since the plant was designed and built e.g. additional commercial premises, large numbers of additional houses. Check the volume of water being treated and the type of treatment process. Flows greater than design capacity will compromise water quality, due to insufficient contact time with UV or overloading of filters for example. If unclear ask the owner of the supply to verify the information from the installer or supplier. | TBC | No risk |  |  | Liverpool City Council
O2 | No | 5 | Is there adequate pre-treatment (e.g. filtration) in place if required? | TBC | Ion exchange is usually preceded by filtration dependant on the quality of the source water and corresponding design of the treatment works. This should remove particulates from the raw water to prevent the media blocking. Evidence of the requirement for pre-treatment or of inadequate pre-treatment is an increased frequency of filter blocking or backwashes being required. | TBC | No risk |  |  | Luton Borough Council
O3 | No | 5 | Is the media depth at a minimum to design specification? | TBC | Confirm with the person responsible for maintenance how they check media depth ( during initial filling and replacing/ toping up the media) and ensure minimum depth is maintained as per the manufacturer's specification. | TBC | No risk |  |  | Maidstone Borough Council
O4 | No | 5 | Is the ion exchange media composition as per design specification? | TBC | Confirm with the person responsible for maintenance whether they understand what the media composition is and whether this was to the manufacturer's specification. | TBC | No risk |  |  | Maldon District Council
O5 | No | 4 | Is there a suitable maintenance schedule? | TBC | Ion exchange units will needs periodic maintenance as specified by the manufacturer. The operator should maintain records to confirm this is being adhered to. | TBC | No risk |  |  | Malvern Hills District Council
O6 | No | 5 | Is the regeneration regime as per design specification? | TBC | Ion exchange units are either cation exchangers that exchange positively charged ions (cations) or anion exchangers that exchange negatively charged ions (anions). These ions need to be replaced periodically by flushing the resin with a solution containing an excess of these ions – typically brine solution containing sodium ions. The frequency will be specified by the manufacturer. The rate at which the operator uses and has to buy fresh solution may be an indication as to whether this regeneration regime is being adhered to. | TBC | No risk |  |  | Manchester City Council
Section P - TREATMENT PLANT: Other Filters | [9 empty] | Mansfield District Council
P1 | No | 5 | Does the plant design take into account the raw water quality? | TBC | The raw water quality at each site will determine the required design of the membrane plant depending on the nature of the water quality challenge. The manufacturer will recommend specific design characteristics and pore sizes for the membranes to remove specific chemical or microbiological contaminants. Ask for evidence that the membrane plant is site-specific. | TBC | No risk |  |  | Medway Council
P2 | No | 5 | Is there adequate pre-treatment to prevent membrane fouling and damage? | TBC | The integrity of the membrane is critical to ensure effective treatment. Therefore the presence of an appropriate pre-treatment is essential to protect the membrane against chemical (e.g. salinity), microbiological, aesthetic contamination or insufficiency of the supply . Pre-treatment must be adequate to prevent fouling and scaling, as well as protecting the membranes from physical damage. There should be suitable protection/screens to neutralise pretreatment oxidants and the operator should provide procedures and records of the operation and monitoring of the membrane to check for integrity. Records should also be kept when membranes are replaced, including when ruptured or damaged. Ask the owner to demonstrate, with suitable documentation that the pre-treatment is adequate. For further information please contact DWI. | TBC | No risk |  |  | Melton Borough Council
P3 | No | 5 | Are the cleaning regimes (for descaling and antifouling, etc.) being followed as set out in the design specification? | TBC | Check the membrane's design manual requirements for specification of the cleaning (antifouling and descaling) regime. The operator should provide evidence to demonstrate compliance with this manual. For further information please contact DWI. | TBC | No risk |  |  | Mendip District Council
P4 | No | 5 | Are the chemicals used in the process as recommended by the manufacturer? | TBC | Any chemicals used in the treatment stage should be specified by the manufacturer and the operator should be asked for evidence that the correct chemicals are in use. Incorrect chemicals could cause membrane damage. For further information please contact DWI. | TBC | No risk |  |  | Merthyr Tydfil County Borough Council
P5 | No | 5 | Is there a procedure to confirm that the integrity of the membrane is maintained? | TBC | The integrity of the membrane is critical to ensure effective treatment. There should be suitable protection/screens to neutralise pretreatment oxidants and the operator should be asked for evidence of how the membrane is checked for integrity. They should also keep records when a membrane is replaced when ruptured or damaged. | TBC | No risk |  |  | Merton
P6 | No | 5 | Are the filters replaced as per the manufacturer's specifications (or more frequently)? | TBC | The manufacturer will specify the frequency at which the filters should be replaced. Ask for evidence that this is being adhered to. | TBC | No risk |  |  | Mid Devon District Council
P7 | No | 5 | Was the raw water quality taken into account when the filters were installed? | TBC | The raw water quality on each supply will determine the filter type, number and size (e.g. 1 micron, 5 micron, etc) depending on the nature of the water quality challenge. The installer should specify this based on quality characteristics of the source water. Ask the owner of the supply if they have details of this specification. | TBC | No risk |  |  | Mid Suffolk District Council
P8 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Mid Sussex District Council
P9 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Middlesbrough Borough Council
Section Q - TREATMENT: Desalination or Reverse Osmosis | Yes | [5 empty] | No risk |  |  | Milton Keynes Council
Q1 | yes | 5 | Is there any likelihood of industrial, domestic or boating waste flows in the vicinity of the water intake to the desalination plant? | TBC | All surface waters, marine and estuarine waters will contain microbial and chemical contamination derived from human activity (industrial, recreational etc.). The location of the abstraction point is key to reducing the levels of such contaminants (including salinity) either by timing when water is drawn or by siting the abstraction point where levels of such contaminants are lower. Knowledge of potential contaminants is important. | TBC | No risk |  |  | Mole Valley District Council
Q2 | yes | 4 | Could any chemical stores potentially contaminate the supply at the intake? | TBC | The hazards may be chemical or aesthetic (taste and odour) contamination. Identify any potential chemicals stored near the intake and their potential impact on the treatment process. Measures include moving intake points, restricting discharges of descaling or antifoaming chemicals, or moving chemical stores. | TBC | No risk |  |  | Monmouthshire County Council
Q3 | yes | 3 | Are there variations in source water levels, which affect the ability to abstract water? | TBC | Such variations may result in insufficiency of supply, and where such circumstances occur the person in control should ensure that alternative supplies or sources are available during these periods. | TBC | No risk |  |  | Neath Port Talbot County Borough Council
Q4 | no | 4 | Is there adequate treatment to prevent membrane fouling and damage? | TBC | Coagulation and micro-filtration pre-treatment are normally used to reduce the impact and fouling of the membranes by particles together with chlorination or biocides to eliminate microbial fouling of membranes. Ensure pretreatment is suitable and adequate to prevent fouling. | TBC | No risk |  |  | New Forest District Council
Q5 | no | 3 | Are oxidants removed during pretreatment? | TBC | Failure to remove oxidants during pretreatment can cause membrane damage. Ensure there is a suitable process to neutralise pretreatment oxidants; monitor membrane integrity and replace when ruptured or damaged | TBC | No risk |  |  | Newark and Sherwood District Council
Q6 | no | 3 | Has the operator mitigated against the demineralisation of the water? | TBC | Water produced from reverse osmosis treatment is low in minerals and therefore aggressive to pipes, and the taste is unacceptable to consumers. It therefore needs to be remineralised which is normally achieved via blending with up to 10% of wholesome water. Evidence that this has not been achieved may be pipe corrosion (higher concentration of metals) or taste problems. | TBC | No risk |  |  | Newcastle-under-Lyme Borough Council
Q7 | yes | 4 | Is the treated supply blended with other sources of drinking water in distribution? | TBC | Blending drinking water from different sources may give rise to water quality issues, such as high mineral levels or aesthetic properties and the water may be more aggressive to pipes. Supplies should be blended in a consistent manner to ensure, amongst other things, that consumer perception is not adversely affected by intermittent and variable blend ratios. | TBC | No risk |  |  | Newcastle-upon-Tyne City Council
Q8 | no | 4 | Are the chemicals used in the process as recommended by the manufacturer? | TBC | Incorrect chemicals can result in less effective treatment or cleaning, or contamination. The person in control must use the chemicals recommended by the manufacturer and ensure they are within use-by dates. | TBC | No risk |  |  | Newham Council
Q9 | no | 5 | Is the plant design appropriate for the nature of the raw water quality? | TBC | The plant design must be capable of meeting the water quality challenges presented by the source water type it is required to treat, i.e. rainwater, seawater, other. Check the manufacturer's specification with the person in control/operator to verify that the treatment arrangements are suitable. | TBC | No risk |  |  | Newport City Council
Q10 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | North Devon District Council
Q11 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | North Dorset District Council
Q12 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | North East Derbyshire District Council
Section R - TREATMENT PLANT: Disinfection: UV | [9 empty] | North East Lincolnshire Council
R1 | No | 5 | Is there adequate preliminary treatment in place? | TBC | Check that the water passing the UV lamp is monitored for turbidity and that turbidity readings do not exceed the acceptable range for the lamp. Ensure that turbidity remains below 1NTU prior to disinfection. Chekc for any evidence of sediment and/or algae build up on the lamp sleeves. | TBC | No risk |  |  | North Hertfordshire District Council
R2 | No | 4 | Is there a validation certificate for the UV system? | TBC | A validation certificate issued on installation should be inspected. Ensure that the device remains effective against target pathogens and check that there have been no changes since the certificate was issued, for example changes in source water quality, flow and demand, number of premises supplied. The validity of the certificate should be challenged where conditions have changed since its installation. | TBC | No risk |  |  | North Kesteven District Council
R3 | Yes | 5 | Can water be supplied if the U.V. is not operational? | TBC | Where UV treatment is installed to mitigate against, for example, the risk of Cryptosporidium then the system should not be operable if the UV is not working. This may be achieved through failsafe mechanisms whereby the supply ceases if the UV stops working. If the UV treatment can be switched off, or bypassed, but water can still be delivered there is a risk that undisinfected water may be supplied. If the system is likely to occasionally shut down, some capacity to store treated water as contingency may be required. | TBC | No risk |  |  | North Lincolnshire Council
R4 | No | 5 | Is the UV operating within its validated range for the product type or lamp? | TBC | Check the UV lamp manual and the specific range for the UV lamp. Can the operator demonstrate that it is operating within this range to address the source water quality challenges. | TBC | No risk |  |  | North Norfolk District Council
R5 | No | 5 | Is the equipment regularly maintained e.g. bulb replacement, cleaning? | TBC | Refer to the maintenance regime recommended by the manufacturer and ask for written documentation that this is being adhered to, including servicing, cleaning the unit and replacing the bulbs. | TBC | No risk |  |  | North Somerset District Council
R6 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | North Tyneside Metropolitan Borough Council
R7 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | North Warwickshire Borough Council
R8 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | North West Leicestershire District Council
Section S - TREATMENT PLANT: Disinfection: chlorination | [9 empty] | Northampton Borough Council
S1 | No | 5 | Is there a backup/standby system for automatic chlorine dosing or an automatic shutdown arrangement? | TBC | Automated chlorine dosing units may operate with a standby system in place, ensuring that chlorine is continued to be dosed at the appropriate level if the main chlorination system fails (for example if the supply runs out, or a dosing line blocks). This will help ensure water is subject to disinfection at all times. | TBC | No risk |  |  | Northumberland County Council
S2 | No | 5 | Is there evidence that maintenance has been carried out of the disinfection system within the last 12 months? | TBC | Refer to the maintenance regime recommended by the manufacturer and ask for written documentation that this is being adhered to, including servicing. Such documentation includes entries in a log book, diary records, and full records. | TBC | No risk |  |  | Norwich City Council
S3 | No | 5 | Is there an appropriate alarm in the event of loss of chlorine dosing? | TBC | Determine what alarms are in place to alert the operator of any loss of chlorine dosing, and whether this is linked to any automatic shut down of the supply to prevent undisinfected water entering the supply. | TBC | No risk |  |  | Nottingham City Council
S4 | No | 3 | Are the chemicals of drinking water grade i.e. approved for use in drinking water supplies? | TBC | Chemicals used in a chlorination system must be approved for use with drinking water supplies and comply with Regulation 5 of the PWS Regulations in England and its equivalent in Wales. | TBC | No risk |  |  | Nuneaton & Bedworth Borough Council
S5 | No | 5 | Is the existing dosing effective? | TBC | Adequate mixing, dosing levels and contact time are important factors for determining disinfection efficacy. Disinfection by-products should be minimised through control of dosing regimes. | TBC | No risk |  |  | Oadby and Wigston Borough Council
S6 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Oldham Metropolitan Borough Council
S7 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Oxford City Council
S8 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Pembrokeshire County Council
Section T - TREATMENT PLANT: Other (answer for any treatment process) | [9 empty] | Pendle Borough Council
T1 | No | 5 | Are all chemicals used for water treatment approved and in date? | TBC | Check all chemicals being used on site to ensure they comply with Regulation 5 and that they are within expiry date. | TBC | No risk |  |  | Peterborough City Council
T2 | No | 4 | Are there controls in place for chemical deliveries to avoid chemicals being added to the wrong storage vessel? | TBC | Check how chemical deliveries are made and ensure there are controls in place to avoid mix up of chemicals e.g. check dosing points are unique, chemical deliveries are always accompanied by competent person, an approved chemical deliverer is employed, or that a chemical specification sheet accompanies any delivery. | TBC | No risk |  |  | Plymouth City Council
T3 | No | 5 | Are chemical injection point(s) protected against potential damage e.g. covered, frost proofing, etc? | TBC | Ask for evidence as to how any dosing point is protected from extremes of weather of physical damage. | TBC | No risk |  |  | Poole Borough Council
T4 | No | 5 | Are there procedures in place to ensure treatment is re-established after any loss of power supply? | TBC | Check there is an adequate procedure in place to restart treatment processes after loss of power, including checks of individual processes to ensure they are working within specification. Some processes such as biological filters may require a period of run to waste. | TBC | No risk |  |  | Portsmouth City Council
T5 | No | 5 | Is there a power back-up or alternative power supply? | TBC | Does the site have a back up generator that is sufficient to power up all the critical treatment processes? Where an alternate power supply is not present; what contingency is in place for the provision of alternate supplies of drinking water? See question Z12. | TBC | No risk |  |  | Powys County Council
T6 | No | 5 | Is the treatment plant adequately protected against vandalism? | TBC | Check perimeter fencing, access gates and the control of the use of any security keys. Other security measures such as patrols and CCTV should be considered depending on the size of the supply. | TBC | No risk |  |  | Preston City Council
T7 | Yes | 5 | Is the site liable to flooding which would result in loss or restriction of treatment process? | TBC | Gauge from surrounding topography if the site is at risk of flooding. Ask the person in control if the site has been flooded in the past. The Environment Agency provide information on flood zones via their and 'What's in my backyard?' website tool. | TBC | No risk |  |  | Purbeck District Council
T8 | Yes | 4 | Could access to the plant be lost or restricted due to weather extremes or other events? | TBC | Gauge from topography and access routes if the site could become isolated during adverse weather. Ask the person in control if the site has been isolated in adverse weather conditions such as flooding or heavy snow. Lack of access during these times may mean essential water quality checks can not be made, or that chemicals stocks can not be replenished. For sites where access is difficult during periods of adverse weather there should be adequate procedures to manage stocks of treatment chemicals and communication with consumers should boil water advice be necessary. | TBC | No risk |  |  | Reading Borough Council
T9 | Yes | 5 | Could adverse weather conditions render the treatment process and/or chemicals ineffective? | TBC | Cold weather can cause dosing lines to freeze and have a direct adverse impact on the efficacy of treatment processes. Pipes should be lagged where appropriate and equipment protected from frost / freezing. During periods of cold weather treatment processes should be checked and there should be adequate contingency procedures should pipes or processes fail. See question U3. | TBC | No risk |  |  | Redbridge
T10 | No | 4 | Are stored chemicals or oil adequately bunded? | TBC | Chemical storage should be contained in a bunded area sufficient to hold all the chemical compound in the event of a burst container. Check there are no drain holes in the bunding and that the containment area is not liable to fill with rain water. This can be a robust solid crate or tub if large enough. | TBC | No risk |  |  | Redcar & Cleveland Borough Council
T11 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Redditch Borough Council
T12 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Reigate and Banstead Borough Council
T13 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Rhondda Cynon Taff County Borough Council
Section U - TREATMENT: Monitoring. Use this section for all treatment systems | [9 empty] | Ribble Valley Borough Council
U1 | No | 5 | Are there appropriate online monitors? | TBC | On-line monitors should be appropriate to any treatment processes present. Where filtration is practiced or UV treatment is in place, turbidity monitors allow the operators to check that filtration is effective in reducing the turbidity levels, so that water presented for disinfection is below 1 NTU. If the supply is chlorinated, a chlorine monitor will ensure that the supply is maintaining the effective chlorine dose for disinfection. If appropriate manual checks are not carried out (with appropriate documentation), on line monitors or an equivalent system should be used. | TBC | No risk |  |  | Richmond upon Thames
U2 | No | 5 | Are they calibrated and maintained? | TBC | Most on-line monitors require regular calibration and occasional maintenance to ensure their measurements are accurate and the person in control of the supply can be assured that the process is operating within specification. The manufacturers should specify the frequency, but as a rule calibration with standards should be at least monthly. If this is carried out through a service agreement with the installer or other contractor, then you should confirm that the number of visits are appropriate and there is evidence the service agreement is being adhered to. | TBC | No risk |  |  | Richmondshire District Council
U3 | No | 3 | Do the on-line monitors have alarms? | TBC | This should be proportionate to the size of the supply - one with two or three domestic dwellings may not require alarms, but a supply with several properties including commercial premises should have alarms on the monitors. If they do, are the trigger levels appropriate? Turbidity on filtered water should alarm at 1NTU as above this any subsequent UV treatment will not be fully effective. If chlorine disinfection is practised, the operator should specify triggers for low or high dose which should alarm if breached to alert them to the fact that either the water is not being adequately disinfected, or that water is being supplied with high levels of chlorine, which may be unacceptable to the consumer. Check what action is taken if the alarm is triggered - is the response time appropriate and is there evidence the procedures are being adhered to. Is there an auto shutdown of the supply if disinfection fails? An auto shut down would be appropriate if no one could hear the alarm and it could not be acted on. | TBC | No risk |  |  | Rochdale Metropolitan Borough Council
U4 | no | 3 | If monitors are not present on the supply, is any on-site testing being carried out? | TBC | If monitors are not present, or they are not linked to alarms, does the operator carry out any routine on-site tests. Typically this should be chlorine levels if chlorine disinfection is carried out, turbidity if filtration and/or UV treatment is in place. On-site testing should be carried out on a routine basis (daily to weekly at a minimum depending on the nature of the source, hazards in the catchment and the population served) and also on a reactive basis, for example if rainwater causes increased turbidity in the source water then additional monitoring should be carried out during and after periods of heavy rain. The extent of the monitoring depends on the nature of the raw water and the upstream distribution network. | TBC | No risk |  |  | Rochford District Council
U5 | no | 3 | Is there a basic schematic for the treatment and monitoring equipment? | TBC | This should at least include locations of the incoming water flow, direction of flow, bypass points, dosing points, treatment type and points, monitor locations, out flow, etc. and materials. | TBC | No risk |  |  | Rossendale Borough Council
U6 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Rother District Council
U7 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Rotherham Metropolitan Borough Council
U8 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Rugby Borough Council
Section V - DISTRIBUTION: Distribution Network | [9 empty] | Runnymede Borough Council
V1 | No | 5 | After treatment is the water fully compliant with quality standards? | TBC | For a PDS this question is only relevant if additional treatment takes place after the point of entry from the public supply. For all other private supplies this can be determined by the examination of sample results, either taken during the risk assessment, during previous risk assessments or through other monitoring arrangements, e.g. EA ground water monitoring surveys, on-site tests. If results indicate that the water is not compliant with quality standards, the control measure(s) must be appropriate to the cause, as indicated by the results, and may require revision of the treatment. | TBC | No risk |  |  | Rushcliffe Borough Council
V2 | Yes | 5 | Are there latrines, septic tanks, waste pipes, animal enclosures or cess pits present in the vicinity of the distribution system? | TBC | If unsewered human or animal sanitation is present within 50m of the distribution system then there is potential for raw human sewage to contaminate the distribution network if there are any defects. Consider any available information on the positioning of septic tanks as well as their condition (maintenance), as well as any available information on the soakaway location in relation to the distribution network. Similarly if there are pit latrines in use, e.g. at a campsite or areas where chemical toilets are discharged, confirm the location of the disposal point or latrine in relation to any clean water pipes. | TBC | No risk |  |  | Rushmoor Borough Council
V3 | Yes | 4 | Is there evidence of disinfection by-products in the network (e.g. taste problems due to THM's)? | TBC | There are many different disinfection by-products but the most commonly analysed-for one is Trihalomethanes (THMs) which is usually identified through sample results. In certain circumstances they may cause taste/odour complaints. This will only be applicable in a Private Distribution system if there is additional treatment after the point of supply and where chloramination or chlorination is present, and such an arrangement should be checked. The presence of THMs is linked to high levels of organic matter in the raw water and/or poor dosing controls during treatment. | TBC | No risk |  |  | Rutland County Council District Council
V4 | No | 3 | If chlorine disinfection is practiced is there a disinfectant residual in the distribution network? | TBC | If chlorine disinfection is practised, determine chlorine residuals through on-site tests. For a private distribution system there may be a residual disinfectant in the network. Answer 'yes' to this question if at least 0.2mg/l is present. | TBC | No risk |  |  | Ryedale District Council
V5 | No | 5 | Is there a suitable written procedure for mains repair and maintenance? | TBC | Relates to the existence of a procedure and how well it ensures protection against contamination i.e. hygienic operations (repairs being carried in a clean environment, fittings disinfected before use, etc.). If no, the likelihood score relates to the frequency of mains repair or other maintenance. | TBC | No risk |  |  | Salford City Council
V6 | Yes | 4 | Is there history of any fractures or faults in the distribution system which could allow ingress of contamination? | TBC | A history of fractures or faults (burst pipes, loss of supplies) could indicate that the pipework is in an unsatisfactory condition or is vulnerable to damage. In a pumped supply this may indicate a lack of pressure control resulting in leaking pipes. Other indicators of existing leaks may be lower than expected chlorine residuals (on a chlorinated supply), high plate counts or other microbial indicators although these may be absent as under normal (pressurised) conditions ingress will not occur. | TBC | No risk |  |  | Sandwell Metropolitan Borough Council
V7 | Yes | 4 | Is there any other route by which contamination can enter the distribution network via back-flow? If there is ponding of surface water or poor drainage, could water be pulled into the system during low pressure or changes in pressure, e.g. backflow from hoses, taps, or standpipes? | TBC | Contamination can also enter the distribution network via back-flow. This comprises back pressure (pushed) or back-siphonage (sucked). Where pressure differentials occur without suitable back-flow or air gap protection then contamination may enter the network through cross connections; leaking joints, broken pipes etc. Back-flow and other suitable fittings (including air gap protection) should be installed on animal watering troughs, standpipes, hoses, commercial premises, for example. If the drinking water is originally from a public supply (i.e. to a PDS or temporary event) the relevant water company or licensee will have responsibility for the enforcement of the Water Fitting Regulations 1999 and should be consulted if any cross connections, back-siphonage and back-flow hazards are identified. | TBC | No risk |  |  | Scarborough Borough Council
V8 | Yes | 4 | Is there evidence any pipes are coal tar lined? | TBC | Coal tar was used pre-1970 to line iron mains. Coal-tar linings can be discounted in plastic, cement mains or asbestos mains. This material contains compounds, amongst others, called polycyclic aromatic hydrocarbons, some of which are known to be carcinogenic above certain concentrations (consult WHO guidelines). Furthermore, coal tar lining can cause various unpleasant aesthetic issues, including petrochemical like taste and odours. Positive evidence for the presence of coal-tar linings may be the analytical results for PAH's or reports of taste and odour. Determine whether any records exist of the presence of coal tar lined mains. If there is any positive evidence of the presence of coal-tar linings, the person in control can confirm any existing control measures and any planned long term remediation. In the absence of any positive evidence, score the likelihood as 1. | TBC | No risk |  |  | Sedgmoor District Council
V9 | Yes | 5 | Do any third parties have access to hydrants or other points in the distribution system? | TBC | Third parties (contractors, builders, tenant farmers etc.) should only have access to hydrants via a procedure of authorised permission to operate them. This should only be granted where risk to disturbing deposits has been assessed as low. Where no such system is in place, an appropriate procedure must be implemented which should include control of their use. | TBC | No risk |  |  | Sefton Metropolitan Borough Council
V10 | Yes | 4 | Is there potential contamination of plastic pipes through designated contaminated land, oil from generators/household fuel tanks/fuel stores or solvent spillage? | TBC | This relates to not only the presence of these types of pipes, but also the possibility that they could be exposed to contamination and migration of the volatiles through the plastic pipes into the water. | TBC | No risk |  |  | Selby District Council
V11 | Yes | 4 | Are there any pipes exposed and at risk of damage by any means e.g. vermin, vehicle, UV/sunlight damage, overheating or freezing? | TBC | Pipes that are laid overground or in shallow trenches may be at risk to damage by gnawing rodents, or accidental damage by other wildlife or livestock or any other means, including those caused by motorised vehicles or machinery. Consider this risk in terms of the pipe material, their position, location, exposure to vermin and other animals, use of surroundings. Freezing or overheating may also occur - regular temperature checks should be undertaken (particularly during extremes of weather, and if overheating regular flushing of the water may help reduce the risk of algal growth, or lagging may help protect from freezing. | TBC | No risk |  |  | Sevenoaks District Council
V12 | No | 2 | If there are valves in the network which are normally closed, are there measures in place to control when and how they are operated? | TBC | Closed valves require periodic operation to prevent them seizing. However, deposits do collect behind them over time and can cause discolouration and turbidity. Therefore such operations must be controlled by an approval procedure, to ensure valve operations are first risk accessed and only carried out by competent persons following an appropriate procedure. | TBC | No risk |  |  | Sheffield City Council
V13 | Yes | 2 | Are there sections of pipework containing stagnant water? | TBC | Characterised by either sections of mains of a relatively large diameter in relation to the demand off it e.g. a 3" main with a trough at the end which is only occasionally used is likely to contain stagnant water; or legs of main with no connections off it therefore no turnover of water or where a low discharge point (i.e. single standpipe). 'Dead legs' of main may be present (no connections off it) which are valved out of the distribution system, which pose a hazard if there are insufficient measures to prevent the valve being operated. | TBC | No risk |  |  | Shepway District Council
V14 | Yes | 3 | Where there is copper pipework present, is it corroding? | TBC | Where copper pipes are used in the distribution system, these problems can be determined through on-site tests, or may manifest in taste complaints (metallic) or discolouration (blue/green) or laboratory tests. | TBC | No risk |  |  | Shropshire Council
V15 | Yes | 5 | Is there the potential for backflow from commercial premises, domestic premises, unauthorised connections, standpipes or unregulated supplies? | TBC | If the premises are within the private supply check whether backflow protection is in place. If the supply is a PDS the appropriate Water Company can confirm whether any existing backflow deficiencies have been identifed upstream of the supply to the PDS. All PWS should follow this best practice with back flow devices being installed. | TBC | No risk |  |  | Slough Borough Council
V16 | Yes | 4 | Are lead pipes present in the supply? | TBC | Lead pipes are usually only found in distribution systems laid before the 1970s. Unpainted lead pipes appear dull grey. They are also soft and if they are gently scraped you will see the shiny, silver-coloured metal beneath. Dissolution of lead into the water supply occurs at a higher rate where the pH of the water is lower (more acidic). If found short term measures include advising the consumers to run the tap before use, especially when the water has been standing in the pipes for longer periods of time (e.g. overnight), longer term measures include replacing the lead pipes. If parts of the distribution system are metallic, potentially laid pre-1970 but the person in control is now aware of their material, a first draw sample for lead may be appropriate to confirm. | TBC | No risk |  |  | Solihull Metropolitan Borough Council
V17 | No | 5 | Do all junctions in the supply network, particularly animal watering systems and standpipes, have backflow protection? | TBC | If there are provisions made to provide water to animal watering troughs or other connections where back-siphonage may occur, e.g. from a hosepipe permanently connected, there is potential for the contents of the trough or container to be back-siphoned into the distribution pipe and for the contents of the trough or container to enter the supply. The contents of a cattle watering trough or a barrel into which the end of a hose is submerged presents a hazard if it enters the supply system. It is essential that where connections are made on the system prior to the first taps to be used for domestic (potable) consumption appropriate back-siphonage prevention devices are fitted. | TBC | No risk |  |  | South Buckinghamshire District Council
V18 | Yes | 5 | Are there any known or potential cross-connections (between different sources, greywater systems, sewage pipes or other waste pipes)? | TBC | There should be a clear site plan or schematic with the location (and direction of flow) of the drinking water, greywater or sewage pipes. There should be clear labelling and pipe specification for the different systems - full details in BS 8515 and WRAS guidance Note 9 - 02 -05. Main water connections to any private water supply must be protected from cross-connection and backflow protection is required on the mains supply. Contact the local water company if this is absent or there are any possible contraventions of the Water Fittings Regulations. | TBC | No risk |  |  | South Cambridgeshire District Council
V19 | Yes | 3 | Have there been complaints or reports of water quality problems (e.g. taste, odours or reports of any aquatic animals (freshwater shrimp, louse or worms)? | TBC | Ask the operator if there have been any complaints about the water being supplied or have known taste, odour or aquatic animal issues. In England and Wales 50% of drinking water is derived from surface water, which contains small plants (algae) and animals. When surface water is treated the majority of these plants and animals are removed. However some animals and algae can pass through water filters and enter the distribution system. During periods of low flow or stagnation in particular colonies of these animals can develop and therefore be present in the water drawn from the tap. Taste and odours issues may arise from certain algal products such as geosmin. | TBC | No risk |  |  | South Derbyshire District Council
V20 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | South Gloucestershire Council
V21 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | South Hams District Council
V22 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | South Holland District Council
Section W - DISTRIBUTION: Storage of treated water in the distribution network (including private distribution systems) | [9 empty] | South Kesteven District Council
W1 | No | 4 | Are all treated water reservoirs covered appropriately e.g. No risk of ingress and/or constructed of suitable material? | TBC | The level of protection for all tanks or similar structures should be equivalent to that recommended for the source itself as the potential for contamination to enter the system via such structures is just as high as for the source itself. | TBC | No risk |  |  | South Lakeland District Council
W2 | No | 4 | Are all treated water reservoirs of sufficient structural integrity to prevent ingress of contamination, including covers? | TBC | Structural cracks and other defects in the roof and sides of the reservoir/tank provide a route of contamination, notably microbiological, via water ingress/rain. The reservoir/tank should be in a good general state of repair. Inspect its condition, looking for points of ingress and weakness, paying particular attention to the roof condition, and areas of notable deterioration or decay, which pose a future risk should the structure come under stress. Where possible carry out internal inspections to determine any points of ingress or potential points of ingress. Flooding the roof during inspections will highlight areas requiring remediation. Any reports from contracted inspections should be consulted to assist with the assessment. | TBC | No risk |  |  | South Norfolk Council
W3 | No | 4 | Is the integrity of the reservoir suitably robust against damage by weather or animals? | TBC | The over all structure of the reservoir should be fit for purpose at all times to ensure any risk to its integrity is not compromised. Consider its position and robustness (including the material it is made of) in terms of its exposure to adverse weather in a worse case scenario and livestock within its vicinity. | TBC | No risk |  |  | South Northamptonshire Council
W4 | Yes | 4 | Are there any waste water pipes, or waste water storage tanks adjacent to the tanks/reservoirs? | TBC | Waste pipes may allow their contents to leach into the soil if damaged and enter the reservoir/tank where its integrity is compromised. Assess available information for example about previous defects, the age of the pipes and their location to determine the likelihood of the hazard presented. Consider whether the pipe(s) could be relocated to lower depth ( avoiding damage) moved to reduce the contamination risk. All contractor on site should be made aware of the location of waste pipes when working on the site. | TBC | No risk |  |  | South Oxfordshire District Council
W5 | Yes | 4 | Are there any unprotected or inadequately protected access covers and/or vents? | TBC | Access covers and air vents present potential routes of ingress of water and other materials, which pose a risk of microbiological contamination and poor aesthetic quality. Vents should be checked to ensure adequate protective mesh is in place to prevent access of vermin and other wildlife, and ingress of general debris (leaves, insects, soil etc). Entry/access covers should be of a robust material, watertight and in a state of good general repair. There should be seals around the opening to the reservoir/tank that are in a sound state of repair (i.e. not in a state of decay, absent or do not provide an adequate seal against ingress). | TBC | No risk |  |  | South Ribble Borough Council
W6 | No | 4 | Are any treated water reservoirs adequately protected against solar heat gain, vandalism (deliberate contamination of treated water and unauthorised access)? | TBC | Reservoirs should be adequately protected against the risk of intentional damage. Covers and access points must be securely locked when not in use and access to these points controlled. Check that the owner has records of all key owners. The reservoir/tank should be suitably robust in structure in a secure location. All tanks must be insulated against solar heat gain or freezing. | TBC | No risk |  |  | South Somerset District Council
W7 | No | 4 | Is there a stock-proof fence around any inspection chambers? | TBC | Inspection chambers must be adequately protected by fences that are of appropriate height, material and robustness. | TBC | No risk |  |  | South Staffordshire District Council
W8 | No | 4 | Are the reservoirs regularly maintained and cleaned with appropriate records? | TBC | Verbal assurance from the owner that a reservoir is regularly cleaned/maintained is not evidence in itself that the action is undertaken or that the frequency is appropriate. Examine any available records, such as log books and/or supporting documentation such as contractual work receipts as evidence and in addition look for physical signs that covers and access points are in regular use for this purpose. Annual cleaning is recommended for a surface water supply and frequency for other sources should be determined as appropriate, based on water quality history and the current risk assessment. Note that this question is not applicable to temporary installations / events. | TBC | No risk |  |  | South Tyneside Metropolitan Borough Council
W9 | No | 3 | Is there a regular turn over of water, such that the capacity of the storage vessel matches demand? | TBC | Water which remains standing for any length of time in a holding structure will deteriorate to varying degrees depending on the conditions it is exposed to. The level of the water within the reservoir/tank should therefore rise and fall at intervals throughout each day facilitating the constant input of fresh water to the structure. Ask the owner to what extent the water is used on a daily basis to determine whether the water turnover is adequate. | TBC | No risk |  |  | Southampton City Council
W10 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Southend-on-Sea Borough Council
W11 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Southwark
W12 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Spelthorne Borough Council
Section X - Premises supplied (applicable to domestic dwelling or commercial premises) | [9 empty] | St Albans District Council
X1 | Yes | 5 | Is the drinking water supply to any customer premises (kitchen tap) supplied via a loft tank? Note; there is no need to inspect loft tanks, just ask for evidence. If no, move on to question X4. | TBC | Many properties served by a private supply, particularly those on smaller supplies, will have a header tank within the property to provide sufficient water pressure for the household and also to act as a balancing tank to equalise the pressure differences experienced in the system when pumps are operating to bring water into the property. However, if the header tank is not properly constructed and protected then any material that may be present in the roof space, whether that be dust or mice or bat droppings, will have the potential to enter the tank and so contaminate the supply. If the property has a header tank which feeds the main domestic (potable) tap, usually the kitchen cold water tap, and that tank is not properly protected then the risk characterisation score should reflect the situation encountered and a “Yes” response entered, and a likelihood of 5. If the header tank is present and unprotected but does not feed the main domestic (potable) tap then the risk assessment can be moderated. If when asked the owner cannot provide the evidence to show the condition, protection and cleaning regime for the tank it must be assumed these factors are not satisfactory and there is a high likelihood of contamination. If this evidence is subsequently provided the score can be reassessed. | TBC | No risk |  |  | St Helens Metropolitan Borough Council
X2 | No | 4 | If yes, do all loft tanks have a robust vermin proof cover? | TBC | The lid should be made of suitable material, exclude light and be tightly fitting and secure, so that birds, vermin and dust cannot get into the water. | TBC | No risk |  |  | Stafford Borough Council
X3 | No | 3 | If yes, is there evidence the loft tanks are cleaned at least once per year? | TBC | Tanks should be inspected once per year and depending on the results, an appropriate cleaning regime put in place. Inspections and cleaning should be recorded. Where no records are currently kept, request the person in control to set them up. | TBC | No risk |  |  | Staffordshire Moorlands District Council
X4 | Yes | 4 | Is there any lead pipe work within the properties? | TBC | High levels of lead in drinking waters are usually caused by the dissolution of lead (plumbosolvency) from lead pipe work, tank linings or use of leaded alloys in water fittings. Traces of lead may also be derived from lead solder and from PVC pipes containing lead-based stabilisers. If the pipe is dull-grey and is easy to scratch leaving shiny marks then it is likely to be lead. The UK drinking water quality regulations specify a standard for lead of 10 μg/l to be met by 2013. For small water supply systems the best approach is the replacement of lead-containing materials with non-leaded alternatives. However treatment methods are available to reduce plumbosolvency. Water that has been standing in lead pipes for long periods, for example overnight, should not be drunk. In these circumstances, the tap should be run for long enough to clear the pipes before taking water for drinking or cooking. | TBC | No risk |  |  | Stevenage Borough Council
X5 | No | 2 | Is the water at the consumers tap clear, taste and odour-free? | TBC | Drinking water should be visually clear and free of exceptional odours at the time of the visit. If on-site turbidity tests are carried out the results should be <4NTU. | TBC | No risk |  |  | Stockport MBC
X6 | No | 5 | Is there adequate backflow protection for any rainwater harvesting systems in place at any of the properties? | TBC | In recent years, rainwater harvesting systems are becoming more prevalent and are often fitted to new build properties by design. There are guidelines about their installation to ensure that there is no risk of contaminating other drinking water supplies to the property which the harvesting system is designed to augment (see BS 8515 - Rainwater harvesting systems Code of Practice ). Where a rainwater harvesting system is installed, the pipe work should be separate to the private supply (no cross-connections), should be clearly labelled, and there should be an air gap (or other suitable backflow protection) where the private drinking supply connects to any chamber which also has a rainwater supply. Where the source to a property is originally public water supplies (i.e. a private distribution system) these requirements are covered by the Water Fittings Regulations 1999, which the local water undertaker has a duty to enforce. Otherwise for a private water supply if there is a rainwater harvesting system installed and the consumer is experiencing taste, odour, discolouration or other aspects of water quality with their drinking water then the Local Authority should ask for records of the system installation to determine that there is no risk of cross contamination. | TBC | No risk |  |  | Stockton on Tees Borough Council
X7 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Stoke-on-Trent City Council
X8 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Stratford-on-Avon District Council
X9 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Stroud District Council
Section Y - Point of use devices ( i.e individual property treatment systems such as UV systems, filter, membrane, Reverse osmosis (RO) under the sink) | [9 empty] | Sunderland City Council
Y1 | No | 5 | Is the treatment system maintained to the manufacturer's instructions (filter changeover, cleaning)? | TBC | A point of use (POU) device is a property specific treatment device. The manufacturers of each treatment unit will specify the frequency and type of maintenance required. Ask the owner for evidence that this is being adhered to. | TBC | No risk |  |  | Surrey Heath Borough Council
Y2 | No | 5 | Is the design of the individual treatment system appropriate for the nature of the raw water quality? | TBC | The water quality at each premises will determine the required point of use treatment dependant on the contaminant that the unit should remove or inactivate. Ask for evidence that the unit(s) is designed for the property. | TBC | No risk |  |  | Sutton
Y3 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Swale Borough Council
Y4 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Swansea City and Borough Council
Y5 | Yes |  |  | N/A | No guidance available |  | No risk |  |  | Swindon Borough Council
Section Z - MANAGEMENT & CONTROL: To determine the risk rating for this section, answer questions Z2 to Z27 to inform the answer to Z1.There should only one risk rating for this section in Z1. | [9 empty] | Tameside Metropolitan Borough
Z1 | No | 5 | CONFIDENCE IN MANAGEMENT? To determine the risk rating for this section, answer questions Z2 to Z27 to inform the answer to Z1.There should only one risk rating for this section in Z1. | TBC | No guidance available | TBC | No risk |  |  | Tamworth Borough Council
Z2 |  |  | Are records kept of key checks e.g. Equipment maintenance, site inspections, on-site tests, etc |  | No guidance available |  |  |  |  | Taunton Deane Borough Council
Z3 |  |  | Are there written procedures for the operation and maintenance of equipment? |  | No guidance available |  |  |  |  | Teignbridge District Council
Z4 |  |  | Are there procedures for responding to alarms, monitors, on-site tests? |  | No guidance available |  |  |  |  | Telford & Wrekin Council
Z5 |  |  | Is there a written procedure for installations, pipe repairs and maintenance to protect against microbial contamination? |  | No guidance available |  |  |  |  | Tendering District Council
Z6 |  |  | Do operators have adequate (even if informal) general hygiene awareness? |  | No guidance available |  |  |  |  | Test Valley Borough Council
Z7 |  |  | Is there a documented procedure for operation of valves including authorisation? |  | No guidance available |  |  |  |  | Tewkesbury Borough Council
Z8 |  |  | Are there any records of reservoir cleaning and maintenance? |  | No guidance available |  |  |  |  | Thanet District Council
Z9 |  |  | Are the records checked to ensure the required maintenance and checks have been carried out satisfactorily? |  | No guidance available |  |  |  |  | Three Rivers District Council
Z10 |  |  | Is there a stock control process for any chemicals used to ensure their continuous availability? |  | No guidance available |  |  |  |  | Thurrock Council
Z11 |  |  | Is there a stock control process for any key spare parts/equipment? |  | No guidance available |  |  |  |  | Tonbridge and Malling Borough Council
Z12 |  |  | Is there a documented contingency plan in the event of power failure, equipment failure? |  | No guidance available |  |  |  |  | Torbay Council
Z13 |  |  | Is the person nominated to manage the supply trained to run and maintain the supply? |  | No guidance available |  |  |  |  | Torfaen County Borough Council
Z14 |  |  | Is there a nominated person to run the supply when the above person is unavailable? |  | No guidance available |  |  |  |  | Torridge District Council
Z15 |  |  | Is there a documented system to report emergencies to management/owner of supply? |  | No guidance available |  |  |  |  | Tower Hamlets
Z16 |  |  | Are there calibration schedules in place for key dosing and monitoring equipment? |  | No guidance available |  |  |  |  | Trafford Metropolitan Borough Council
Z17 |  |  | Is there a weekly site inspection to check for changes (e.g. Dead sheep, broken fence)? |  | No guidance available |  |  |  |  | Tunbridge Wells Borough Council
Z18 |  |  | Are there appropriate procedures for rectifying customer complaints? |  | No guidance available |  |  |  |  | Uttlesford District Council
Z19 |  |  | Are there procedures and records in place to inform the LA of any changes to the risk assessment? |  | No guidance available |  |  |  |  | Vale of Glamorgan Council
Z20 |  |  | If a risk assessment has previously been carried out, is there a plan for delivering the required improvements? |  | No guidance available |  |  |  |  | Vale of White Horse District Council
Z21 |  |  | Is there a detailed plan of the site including details of source, tanks, distribution pipes, valves (material, age) etc. |  | No guidance available |  |  |  |  | Wakefield Metropolitan District Council
Z22 |  |  | Is there a documented contingency for the supply running out? |  | No guidance available |  |  |  |  | Walsall Metropolitan Borough Council
Z23 |  |  | Do the treatment chemicals and materials conform to Regulation 5? Have all new installations since 2010 complied with Regulation 5 (or equivalent in Wales) – products and processes |  | No guidance available |  |  |  |  | Waltham Forest
Z24 |  |  | Do all materials involved in the distribution system conform to Regulation 5? Have all new installations since 2010 complied with Regulation 5 (or equivalent in Wales) – products and processes? |  | No guidance available |  |  |  |  | Wandsworth
Z25 |  |  | Is there a documented procedure for carrying out mains tappings (making new connections into pipes)? |  | No guidance available |  |  |  |  | Warrington Borough Council
Z26 |  |  | Are persons carrying out this work competent and trained in this procedure?(e.g. approved by a water company or part of the Water Safe Scheme)? |  | No guidance available |  |  |  |  | Warwick District Council
Z27 |  |  | Any additional site specific hazard(s) associated with management |  | No guidance available |  |  |  |  | Watford Borough Council
Waverley Borough Council
Wealden District Council
Wellingborough Borough Council
Welwyn Hatfield District Council
West Berkshire District Council
West Devon Borough Council
West Dorset District Council
West Lancashire District Council
West Lindsey District Council
West Oxfordshire District Council
West Somerset District Council
West Suffolk Council
Westminster City Council
Weymouth and Portland Borough Council
Wigan Metropolitan Borough Council
Wiltshire Council
Winchester City Council
Windsor and Maidenhead
Wirral Metropolitan Borough Council
Woking Borough Council
Wokingham Borough Council
Wolverhampton City Council
Worcester City Council
Worthing Borough Council
Wrexham County Borough Council
Wychavon District Council
Wycombe District Council
Wyre Borough Council
Wyre Forest District Council
York City Council